## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0005_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0998 |  |  | Transmital Date: 24-May-2022
Document Title: Data Sheets For LV Switchgear |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0998 |  |  | Transmital Date: 24-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0005_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | دمای محیطی مطابق مدرک پایه به 52درجه سانتی گراد افزایش یابد. |  | 1401-2294-96604 | 1401-03-21 | ماکزیمم دمای محیط در بند دو از دو به 52 درجه افزایش یافت.
2 | تغذیه مدارات سیگنالینگ نیز می بایست از طریق ترانس ایزوله انجام گردد تعداد ترانس های ایزوله به تعداد cubicle ها در نظر گرفته شود. |  | 1401-2294-96604 | 1401-03-21 | اعمال گردید
3 | تغذیه مدارات سیگنالینگ کلید های ورودی 110VDC لحاظ گردد. |  | 1401-2294-96604 | 1401-03-21 | نوت شماره 6 در انتهای مدرک اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-May-22 |  |  |  |  | Date: