## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0003-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0880 |  |  | Transmital Date: 30-Apr-2022
Document Title: Existent MV Switchgear Expansion Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0880 |  |  | Transmital Date: 30-Apr-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0003-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | فایرکنترل پانل محلی حذف گردد و بجای آن از LCSاستفاده گردد NOTE 6 نیز برهمین اساس اصلاح شود . |  | 01/2294/85203 | 1401/03/10 | بر اساس اطلاعات گرفته شده از بخش مکانیک و سازندگان سیستم آتش نشانی، کنترل این سیستم از طریق فایل کنترل محلی است که توسط سازنده تأمین می گردد. بر همین اساس موتور آتش نشانی از طریق LCS روشن نمی شود. چراکه با توجه به فشار خط آب این عمل صورت میگیرد.
2 | با توجه به اینکه حفاظت های الکتروموتور پمپ آتش با الکتروموتور کمپرسورهای گاز تفاوت دارد، لذا از نظر تیپ فیدر موتوری نیز متفاوت در نظر گرفته می شود. |  | 01/2294/85203 | 1401/03/10 | تیپ موتوری C5 برای پمپ آب آتش نشانی به صورت مجزا در نظر گرفته شد. لازم به ذکر است فیدر ورودی به ترانس آب آتش نشانی تیپ C2 و فیدر ورودی به موتور آب اتش نشانی تیپ C5 می باشد.
3 | فیدر ترانس واسطه مربوط به پمپ آتش نشانی از طریق RCP قطع و وصل شود . |  | 01/2294/85203 | 1401/03/10 | فیدر ترانس واسطه همانند فیدرهای ترانسی از طریق RCP قطع و وصل می گردد.
4 | جهت فیدر های ترانسی رله مربوط به اینترلاک بالادست و پایین دست از نماد 94استفاده شود و در بخش LEGENGDنقشه نیز عبارت 94-Intertrip receive relay درج گردد. |  | 01/2294/85203 | 1401/03/10 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-May-22 |  |  |  |  | Date: