## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-RT-0005-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0761 |  |  | Transmital Date: 29-Mar-2022
Document Title: 33KV OVER HEAD LINE STUDY REPORT |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0007-EL-TR-0761 |  |  | Transmital Date: 29-Mar-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-RT-0005-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مقدار Creepage Distance بر اساس استاندارد 100 به 40 میلی متر بر کیلوولت اصلاح گردد. |  | 1401-2294-47897 | 1401-02-11 | در صفحه 8 بخش 6.2 اصلاح گردید.
2 | مرجع استخراج فرمولهای استفاده شده در مدرک جهت بررسی ارسال گردد. |  | 1401-2294-47897 | 1401-02-11 | همانگونه که در بخش 3 مدرک NORMATIVE REFERENCES معرفی شده، مرجع تمامی فرمول ها نشریه های شرکت توانیر می باشند که نشریه شماره 374 (مشخصات فنی عمومی و اجرایی خطوط توزیع) نیز به این بخش اضافه گردید. (به طور نمونه؛ رجوع گردد به صفحه 17 نشریه 402 و صفحه 73 نشریه 374)
3 | علت استفاده از دکل های دو مداره چیست؟ |  | 1401-2294-47897 | 1401-02-11 | دکل های مورد استفاده در طرح، دکل های تیپ A-B-C خطوط توزیع می باشند که به هر دو صورت دو و تک مداره با همین نام تولید و مورد استفاده قرار میگیرند. با این حال، نقشه ها در بخش 10 به صورت تک مداره اصلاح گردید.
4 | کاتالوگ مربوط به مقره های استفاده شده در بخش 6.4 اراده شود. |  | 1401-2294-47897 | 1401-02-11 | پیوست گردید.
5 | در مدرک مربوط به خط 33 چرا فقط یک نوع دکل ارائه شده است. |  | 1401-2294-47897 | 1401-02-11 | پیرو توضیحات بند 3، نقشه ها در بخش 10 مدرک خط 33 کیلوولت نیز به صورت تک مداره اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 25-Oct-21 |  |  |  |  | Date: