## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0003-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0880 |  |  | Transmital Date: 30-Apr-2022
Document Title: Existent MV Switchgear Expansion Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0880 |  |  | Transmital Date: 30-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0003-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Type C3 spare feeder has not been considered in single line diagram, please clarify. It is recommended type C2 spare feeder on BUS A modified to type C3. Meanwhile motor symbol and related capacitor bank for motor type feeder on BUS B shall be shown. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | مطابق با شرح کار پروژه دو عدد فیدر Spare باید در نظر گرفته شود. یکی متعلق به فیدر ترانسی است و دیگری متعلق به فیدر کمپرسور می باشد. فیدر Spare بر روی باسبار A به صورت C3 در نظر گرفته شده است. لازم به ذکر است با توجه به اینکه ظرفیت بار الکتریکی که در آینده به آن متصل می شود، در این مقطع از پروژه مشخص نیست، لذا امکان محاسبه ظرفیت خازن مورد نیاز وجود ندارد. |  |  | Noted and Closed.
2 | According to following explainations note 4 shall be modified: Protections consist of required protections for power cable and 27R function shall be considered in 3.3KV panel. All other requiered protection shall be considered in fire water local panel. (Shall be clarified by vendor in purchasing orders.) Meanwhile according to above mention items, feeder type shall be modified to C2 instead of C3. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | نوت شماره 4 از مدرک حذف گردید. همچنین خروجی فیدر 11 کیلوولت به سمت ترانس پمپ آب آتش نشانی تیپ C2 و خروجی ترانس به سمت موتور آب آتش نشانی تیپ C3 خواهد بود. |  |  | Noted and Closed.
3 | fire water pump capacitor bank conection point shall be rechecked and investigated from the technicaly point of view. It is proposed to compensate at 3.3kV bus. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | مطابق با ویرایش اول و بر اساس محاسبات انجام شده بر روی مدرک بانک خازنی، در شرایط اضطرار نیاز به در نظر گرفتن بانک خازنی برای این تجهیز نمی باشد. پیرو مذاکرات انجام شده با آن کارفرمای محترم و توضیحات مشاور مبنی بر اینکه در شرایط اضطرار آتش سوزی در سایت و فعال شدن موتور آب آتش نشانی، اصلاح ضریب قدرت در دستور کار نیست، بانک خازنی با موافقت آن کارفرما حذف گردید. |  |  | See below item 9.
4 | Voltage and current sample for capacitor bank shall be shown. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | به صورت یک نوت در نظر گرفته شده است که توسط سازنده لحاظ می گردد. |  |  | Noted and Closed.
5 | CT current rating (2x250/1/1) for spare feeders on BUS B shall be checked and modified. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | اصلاح گردید |  |  | Noted and Closed.
6 | MV Capacitor banks size shall be modified base on NISOC and PEDCO comments on capacitor bank sizing document. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | بر اساس مدرک محاسباتی بانک خازنی و مدارک پایه، توان راکتیو مورد نیاز کمپرسورها 600 کیلووار می باشد که در مدرک اعمال گردید. |  |  | Noted and Closed.
7 | Cable size and length shall be added after finalizing or minor comments on cable sizing and cable list. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | بعد از نهایی سازی مدرک محاسبه کابل، سایز دقیق کابلها در این مدرک لحاظ خواهد شد. |  |  | Will be checked later.
8 | Voltmeter have been considered for all outgoing fedders in the table bellow SLD but existing outgoing feeders had not voltmeter. It shall be rechecked and modified if required. |  | BK-SUR-ENG-ELE-00-02785 | 2022-01-23 | بر اساس مذاکرات تلفنی انجام شده، ولت متر و مبدل ولتاژی بر روی مدرک اصلاح گردید. |  |  | See below item 10.
9 | See above item 3: Fire water capacitor bank shall be deleted after approval of NISOC. |  | BK-SUR-ENG-ELE-00-03635 | 2022-03-16 | حذف شده است. |  |  | Noted and Closed.
10 | See above item 8: According to our telephone conversation, outgoing feeders has not voltmeter. But has been considered in table (Refer to VOLT-METER row). It shall be deleted in table. It shall be checked and modified for surge arraster of C2 type feeders too. |  | BK-SUR-ENG-ELE-00-03635 | 2022-03-16 | اعمال گردید. |  |  | Noted and Closed.
11 | Category of spare feeder on bus B shall be modified to C3 instead of C2. |  | BK-SUR-ENG-ELE-00-03635 | 2022-03-16 | اعمال گردید. |  |  | Noted and Closed.
12 | The connection of MV capacitor bank and protection of C3 type feeders shall be specified base on NISOC letter No. 443266 date 1400.12.19 after Site visit. |  | BK-SUR-ENG-ELE-00-03635 | 2022-03-16 | مطابق با کامنت بر روی مدرک Existent MV Switchgear Expansion Single Line Diagram برای بانک خازنی فیوز-ارت سوییچ-برقگیر در نظر گرفته شده است. |  |  | See below item 13.
13 | According to site visit date 1401.01.23 and previous telephone conversation, the simulation shall be done and the compressor feeders protection shall be rechecked and modified base on NISOC letter NO. 00/2294/443266 date 1400/12/19. (If required) |  | BK-SUR-ENG-ELE-01-04218 | 2022-05-10 | اعمال خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-May-22 |  |  |  |  | Date: