## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0002-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0949 |  |  | Transmital Date: 15-May-2022
Document Title: Electrical Typical Schematic Diagrams For LV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0949 |  |  | Transmital Date: 15-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DG-0002-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | محل انشعاب رله PHC به قبل از کنتاکتور و بعد از سوییچ فیوز جابجا شود. |  | 1401-2294-92391 | 1401-03-17 | مطابق با کامنت شماره 2 کارفرمای محترم مبنی بر استفاده از MPR برای فیدرهای موتوری بالای 30 کیلووات، رله PHC فقط برای تیپ موتوری M3 قابل استفاده خواهد بود که آن هم به قبل از کنتاکتور و بعد از سوییچ فیوز منتلق گردید. برای فیدرهای موتوری توان بالا، این رله درون MPR وجود دارد.
2 | برای فیدرهای موتوری بزرگتر یا مساوی 30 کیلووات از رله MPR استفاده گردد، نماد مربوط به رله MPR نیز در جدول LEGEND درج گردد. |  | 1401-2294-92391 | 1401-03-17 | اعمال گردید.
3 | پیرو بند 20 نامه شماره 00/2294/393495 مورخ 1400/11/13 جهت هر سلول می بایست یک ترانس ایزوله در نظر گرفته شود،در مدرک جهت هر باس یک ترانس در نظر گرفته شده که می بایست اصلاح و به تعداد هر ردیف سلول افزایش یابد. |  | 1401-2294-92391 | 1401-03-17 | درخواست مد نظر کارفرمای محترم به صورت نوت در صفحه 3 لحاظ شده است. لازم به ذکر است بعد از نهایی شدن قرارداد با سازنده تعداد Cubicle مشخص خواهد گردید. از اینرو با توجه به وجود این بند در نوت شماره 2، سازنده موظف به در نظر گرفتن ترانس ایزوله برای هر Cubicle خواهد بود.
4 | بند 8 نامه شماره 00/2294393495 مورخ 1400/11/13 بقوت خود باقی است ،در این مدار در حالت تست ، امکان چک کردن حفاظت ها وجود ندارد. |  | 1401-2294-92391 | 1401-03-17 | حاالت تست جهت چک نمودن حفاظت نیز در نظر گرفته شد. و حفاظتها به قبل از وصل شدن کلید تست منتقل گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 28-May-22 |  |  |  |  | Date: