## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0001-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0884 |  |  | Transmital Date: 30-Apr-2022
Document Title: Electrical Typical Schematic Diagrams For MV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0884 |  |  | Transmital Date: 30-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0001-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Voltage and current sample for capacitor bank shall be shown. |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | به مانند مدرک دیاگرام تک خطی این نوت اضافه گردید |  |  | Noted and Closed.
2 | Voltage level of voltage sample for transducer shall be modified on page 4 (10V shall be modified to 110V). |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | به ولتاژ 110 ولت تغییر پیدا کرد |  |  | Noted and Closed.
3 | 86 lock out relay in protection unit shall be deleted on page 5. (Separeted lock out relay has been considered) |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | اعمال گردید |  |  | Noted and Closed.
4 | ESD Trip have not been shown. It shall be clarified. |  | BK-SUR-ENG-ELE-00-02786 | 2022-01-23 | این تریپ نیز نشان داده شد. |  |  | Noted and Closed.
5 | No Comments. |  | BK-SUR-ENG-ELE-00-03606 | 2022-03-15
6 | No Comments. NOTE: Control circuit correct functionality is not correct and shall be rechecked and modified in the Manufacturer drawings |  | BK-SUR-ENG-ELE-01-04237 | 2022-05-11 | بعد از نهایی سازی قرارداد تابلو، سازنده موظف به تعیین عملکرد صحیح مدارات می باشد که در آن زمان مور بررسی قرار خواهد گرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 11-May-22 |  |  |  |  | Date: