## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DG-0002-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0949 |  |  | Transmital Date: 15-May-2022
Document Title: Electrical Typical Schematic Diagrams For LV panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0949 |  |  | Transmital Date: 15-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DG-0002-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | "LV Switchgear Single Line Diagram " shall be issued before this document and this document shall be revised after finalizing or minor comments on "LV Switchgear single Line Diagram". |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | هر دو مدرک دیاگرام تک خطی و اسکماتیک ارسال شده است. در صورت لزوم مدارک بر اساس کامنتهای جدید مورد بازنگری قرار خواهد گرفت. |  |  | Noted and Closed.
2 | Integrated protection unit so that operate with separated lock out relay shall be considered for incomings and couplers. (For this size of panel built in protection functions in the circuit breaker is not acceptable). For outgoing ACB type (If any), ACB with LSIG protection should be used. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | لحاظ گردید. |  |  | Noted and Closed.
3 | Motor outgoing feeders shall be protected by on load switch disconnecting fuse not fuse. Meanwhile, all switch disconnecting fuse shall be equipped with a striker pin so that their operation causes the contactor to disconnect. In addition, an independent signal light should be considered for its operation on the starter door. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
4 | Over load relay rating above 72 ampere shall be C.T. operated. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
5 | According to electrical system design criteria, each motor starter/feeder will have a 400/230 V isolating transformer for control circuits, so it shall be deleted from related pages and shall be shown on outgoing feeders. (Consideration shall be given control voltage for incomings feeders and couplers will be supplied by DC UPS) |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | یک نوت با این عنوان در صفحه سوم اضافه گردید. برای هر کوبیکل LV یک عدد ترانس ایزوله خشک جهت برق مدار فرمان در نظر گرفته شده است. لازم به ذکر است مدار فرمان ورودیها و کوپلر از برق DC تغذیه می شود. |  |  | Noted and Closed.
6 | Phase Sequence or Phase Balance Relay (47) shall be added for motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | تعداد تیپ های موتوری از 4 عدد به 3 عدد کاهش پیدا کرد. از اینرو تمامی فیدرهای موتوری بالای 18.5 کیلووات دارای MPR می باشد.که درون MPR فانکشن 47 وجود دارد. |  |  | Noted and Closed.
7 | Protection shall be modified and considered base on electrical system design criteria and IPS-E-EL-100(1). (For example 50BF, 50, 51, 50N, 51N, 71, etc shall be added for incoming feeders and transformers.) |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
8 | Technical characteristics, related protection, Local Panel and DGCB for diesel generator shall be shown. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | کلید دیزل، تابلو ی مربوط و حفاظت، مطابق با استاندارد اضافه گردید. |  |  | Noted and Closed.
9 | Emergency stop and start pushbutton shall be considered for all incomings, coupler and outgoing feeders on switchgear front. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | یک نوت با این عنوان در صفحه سوم اضافه گردید |  |  | Noted and Closed.
10 | Voltage sample for capacitor bank shall be shown. Meanwhile CT of capacitor bank shall be located in middle phase. Tag of Capacitor bank (A or B) shall be specified too. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
11 | According to basic LV single line diagram rated current of LV bus bar shall be considered 2000A, instead of 1600A. Meanwhile the rated current of emergency bus bar on page 21 has been mentioned 800A. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
12 | Considered separated lockout relay for ACB shall be deleted. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
13 | According to IPS-M-EL-143, clause 9.6.3: The heaters shall be fed from dedicated power supply. This power supply system may be energized from a dedicated heater panel, independent distribution panel. The panels feeding the heaters in one section of the switchgear shall be fed from the opposite section of the bus bar. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | این بند از استاندارد به صورت یک نوت در شیت 3 اضافه گردید. |  |  | Noted and Closed.
14 | According to IPS-M-EL-143, clause 9.6.4: Heater/s in each cubicle shall be protected by a miniature circuit breaker and an earth leakage protection device or residual circuit breaker of 30mA sensitivity. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | زراین بند از استاندارد به صورت یک نوت در شیت 3 اضافه گردید. |  |  | Noted and Closed.
15 | It is necessary to use three-winding PT for incomings feeders to provide voltage sample for voltage protections, measuring unit and voltmeter. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
16 | 74TCS shall be added to this document and a separted signal lamp shall be considered for incomings and couplers. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
17 | Status to DCS shall be shown for bus tie, all incomings and outgoing motor type feeders. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
18 | Following items shall be added or modified in SLD: -Frequency added in measuring unit -Switchgear tag shall be added -Alarm window and related note shall be added. (This note shall be added: Alarm window shall be equiped with acknowledge and reset button.) -Type of connection (Hardwire/Serial Link) between measuring unit and DCS shall be shown. -Selector switch of incomings and bus bars shall be able to show single phase voltage (added as note) -74TCS and other current protection shall be considered in integrated protection unit and then shall be connected to 86 lock out relay. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | See below item 29.
19 | Following items shall be checked and modified: (Pages 22~25) -64R is not applicable for this project and shall be deleted. -86 lock out relay shall be operated by current protections such as 50, 51, 50N,51N, 50G, … . -27&27R shall be added to TRIP circuit of CB. -Emergency stop and start pushbutton shall be shown on close circuit -ANSI code for O.L relay of transformer (49) shall be added. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | See below item 30.
20 | Current and voltage fault signal lamp shall be considered separately. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | این بند به صورت یک نوت در مدرک اضافه گردید. |  |  | See below item 31.
21 | Voltmeter and ammeter shall be considered for incoming feeder of diesel generator. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | See below item 32.
22 | Technical characteristics of Corbalance CT shall be added and specified. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | کوربالانس مربوط بهMPR در زمان خرید توسط سازنده مشخص می گردد. |  |  | Noted and Closed.
23 | Description of symbols shall be rechecked and modified. (For example MCCB shall be modified in ACB 4 pole description on pages 4) |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
24 | All symbols such as core balance CT and 50G relay shall be added and specified on symbol pages. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
25 | Note1 for ammeter on pages 7&8 and 10&11 has not been mentioned. It shall be clarify. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
26 | Complementry comments will be submitted after receive prerequisit and revised document. |  | BK-SUR-ENG-ELE-00-02412 | 2021-12-25 | متعاقبا اعمال می گردد. |  |  | Noted and Closed.
27 | Interlock and intertrip between upstream (11kV switchgear) and downstream circuit breakers can be connected directly without pass throw IRP. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
28 | As per NISOC Comment CB in the DGCP shall be normal open and ACB in the MCC shall be considered Normal Close |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
29 | Ref. above item 18: There is conflict between this document and single line diagram from point of view type of connection between measuring unit and DCS. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
30 | Ref. above item 19: Following items shall be rechecked and modified: -64R is not applicable for this project and shall be deleted. -86 lock out relay shall be operated by current protections such as 50, 51, 50N,51N, … . -27&47 shall be added to TRIP circuit of CB. -Emergency stop and start pushbutton shall be shown on close circuit |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
31 | Ref. above item 20: Despite the consultant response, has not been mentioned on note page. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | خطا های جریانی و ولتاژی جداگانه چراغ سیگنال شده اند. |  |  | Noted and Closed.
32 | Ref. above item 21: Despite the consultant response, ammeter has not been considered for incoming feeder of diesel generator. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
33 | According to our telephone conversation, mechanical transformer protections (63,71,26) shall be connected to Seperat lock out relay (Flagged and Locked Send&Receive Relay ) in LV switchgear. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
34 | The ammeter in feeder type F2, shall be checked and deleted (If required). There is conflict between this page and outgoing feeder type 2 in single line diagram. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | در نقشه تک خطی آمپرمتر اضافه گردید. |  |  | Noted and Closed.
35 | in the schematice type F3 and F6, Trip circuit need to recheck deu to 50Gf and MCCB trip Normal close contact are series instead of parallel. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | دلیل سری بودن کنتاکتها NO FAULT می باشد که به صورت NC نمایش داده شده است و با توجه به به اینکه کنتاکت NC رله شیشه ای سر راه چراغ سیگنال می باشد ، در صورت بروز خطا چراغ سیگنال روشن می شود. |  |  | Noted and Closed.
36 | in the schematice type F3 and F6, please clarify about "S" normal open contact befor shunt trip |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | حرف اضافه حذف گردید. |  |  | Noted and Closed.
37 | In Schematic type "M1,M2,M3" remote start command shall be modified to "ST DCS". |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | اعمال گردید |  |  | Noted and Closed.
38 | In Schematic type "M1,M2,M3" motor stop status signal shall be considered to sending to the DCS via IRP as per project P&IDs. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | سیگنال و فرمان های مورد نیاز به صورت زیر است: Local/Remote Status Running Status Fault Status Start Command Stop Command Trip Command |  |  | Noted and Closed.
39 | In Schematic type "M3" trip contacts "OL", "50G", "47" shall be connected in parallel. |  | BK-SUR-ENG-ELE-01-04003 | 2021-12-25 | دلیل سری بودن کنتاکتها NO FAULT می باشد که به صورت NC نمایش داده شده است و با توجه به به اینکه کنتاکت NC رله شیشه ای سر راه چراغ سیگنال می باشد ، در صورت بروز خطا چراغ سیگنال روشن می شود. |  |  | Noted and Closed.
40 | No Comments. NOTE: Control circuit correct functionality is not correct and shall be rechecked and modified in the Manufacturer drawings |  | BK-SUR-ENG-ELE-01-04447 | 2022-05-28 | بعد از انجام قرارداد و مشخص شدن سازنده، موارد باقی مانده در جلسات شفاف سازی با وندور نهایی خواهد شد. و در مدرک لحاظ می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 28-May-22 |  |  |  |  | Date: