## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0015_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1030 |  |  | Transmital Date: 01-Jun-2022
Document Title: Data Sheets For Remote Control Panel |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1030 |  |  | Transmital Date: 01-Jun-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0015_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق با مکاتبات قبلی ماکزیمم دمای محیطی 52 درجه سانتی گراد در نظر گرفته شود. |  | 1401-2294-111560 | 1401-03-31 | ماکزیمم دمای محیط به 52 درجه افزایش پیدا کرد.
2 | ولتاژ سیستم کنترل 110 VDC لحاظ شود. |  | 1401-2294-111560 | 1401-03-31 | ولتاژ سیستم کنترل به 110 VDC تغییر یافت.
3 | سلکتور سوییچ به صورت Open-Off-Close در نظر گرفته شود. |  | 1401-2294-111560 | 1401-03-31 | سلکتور سوییچ به صورت Open-Off-Close تغیر یافت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 15-Jun-2022 |  |  |  |  | Date: