## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0016_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0965 |  |  | Transmital Date: 17-May-2022
Document Title: Data Sheets For Distribution & Lighting Panels |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0965 |  |  | Transmital Date: 17-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0016_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 1.2: دمای محیطی به C ° 52 افزایش یابد |  | 1401-2294-93978 | 1401-03-18 | دمای ماکزیمم به 52 درجه افزایش یافت.
2 | بند 3.7: مربوط به ولتاژ کنترل ،عبارت 230VAC از طریق ترانس ایزوله قید گردد. |  | 1401-2294-93978 | 1401-03-18 | در نظر گرفتن ترانس ایزوله در صورت نیاز قید گردید.
3 | بند 4.1: عبارت Self-Standing نیز اضافه گردد |  | 1401-2294-93978 | 1401-03-18 | عبارت Self-Standing (خود ایستا) مربوط به تابلوهایی است که بر روی زمین و بدون نیاز به ساپورت مانند تابلوهای LV و MV قرار میگیرند. ولی این تابلوهای توزیع محلی یا بر روی دیوار نصب می شوند و یا بر روی ساپورت. از اینرو عبارت Self-Standing به آنها اطلاق نمی شود.
4 | بند 4.5: عبارت Current LimitingType ،25KA،4Pole،MCC قید گردد |  | 1401-2294-93978 | 1401-03-18 | با توجه به اینکه در این بندها به مدرک تک خطی اشاره شده است، ذکر دو نکته ضروری است: 1- هر گونه تغییری در مدرک تک خطی این مدرک را تحت تأثیر قرار میدهد. به عبارتی دیگر با توجه به تغییرات زیاد مدارک تک خطی، با هر بار ویرایش جدید آن، مدرک دیتاشیت نیز باید تغییر یابد. 2- در هنگام خرید تابلوهای توزیع محلی و تولید مدرک MR آن، مدارک تک خطی پیوست می گردد که سازنده موظف به تبعیت ساخت از مدارک تک خطی می باشد. از اینرو خواهشمند است از در نظر گرفتن موارد مذکور به صورت دقیق صرف نظر گردد و سازنده به مدرک تک خطی مراجعه نماید.
5 | بند5.5: عبارت Thermal over load( 49) & Instantaneous 0/C ( 50) قید گردد |  | 1401-2294-93978 | 1401-03-18 | این عبارات اضافه گردید.
6 | بند 6.3: مقدار 690V درج گردد |  | 1401-2294-93978 | 1401-03-18 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: