|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **طرح نگهداشت و افزایش تولید 27 مخزن** | | | | | | | |
| **HVAC CALCULATION NOTE FOR CONTROL BUILDING**  **نگهداشت و افزایش تولید میدان نفتی بینک** | | | | | | | |
|  | |  |  |  |  |  |  |
|  | |  |  |  |  |  |  |
|  | |  |  |  |  |  |  |
| D01 | | JUL. 2022 | IFA | H.Adineh | M.Fakharian | M.Mehrshad |  |
| D00 | | MAR. 2022 | IFC | H.Adineh | M.Fakharian | M.Mehrshad |  |
| **Rev.** | | **Date** | **Purpose of Issue/Status** | **Prepared by:** | **Checked by:** | **Approved by:** | **CLIENT Approval** |
| **Class: 2** | | | **CLIENT Doc. Number:** **F0Z-708865** | | | | |
| **Status:** | | **IDC: Inter-Discipline Check**  **IFC: Issued For Comment**  **IFA: Issued For Approval**  **AFD: Approved For Design**  **AFC: Approved For Construction**  **AFP: Approved For Purchase**  **AFQ:** Approved For Quotation  **IFI: Issued For Information**  **AB-R: As-Built for CLIENT Review**  **AB-A: As-Built –Approved** | | | | | |

**REVISION RECORD SHEET**

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **PAGE** | **D00** | **D01** | **D02** | **D03** | **D04** |  | **PAGE** | **D00** | **D01** | **D02** | **D03** | **D04** |
| **1** | X | X |  |  |  | **66** |  |  |  |  |  |
| **2** | X | X |  |  |  | **67** |  |  |  |  |  |
| **3** | X | X |  |  |  | **68** |  |  |  |  |  |
| **4** | X | X |  |  |  | **69** |  |  |  |  |  |
| **5** | X | X |  |  |  | **70** |  |  |  |  |  |
| **6** | X | X |  |  |  | **71** |  |  |  |  |  |
| **7** | X | X |  |  |  | **72** |  |  |  |  |  |
| **8** | X | X |  |  |  | **73** |  |  |  |  |  |
| **9** | X | X |  |  |  | **74** |  |  |  |  |  |
| **10** | X | X |  |  |  | **75** |  |  |  |  |  |
| **11** | X | X |  |  |  | **76** |  |  |  |  |  |
| **12** | X | X |  |  |  | **77** |  |  |  |  |  |
| **13** | X | X |  |  |  | **78** |  |  |  |  |  |
| **14** | X | X |  |  |  | **79** |  |  |  |  |  |
| **15** | X | X |  |  |  | **80** |  |  |  |  |  |
| **16** | X | X |  |  |  | **81** |  |  |  |  |  |
| **17** | X | X |  |  |  | **82** |  |  |  |  |  |
| **18** | X | X |  |  |  | **83** |  |  |  |  |  |
| **19** | X | X |  |  |  | **84** |  |  |  |  |  |
| **20** | X | X |  |  |  | **85** |  |  |  |  |  |
| **21** | X | X |  |  |  | **86** |  |  |  |  |  |
| **22** | X | X |  |  |  | **87** |  |  |  |  |  |
| **23** | X | X |  |  |  | **88** |  |  |  |  |  |
| **24** | X | X |  |  |  | **89** |  |  |  |  |  |
| **25** | X | X |  |  |  | **90** |  |  |  |  |  |
| **26** | X | X |  |  |  | **91** |  |  |  |  |  |
| **27** | X | X |  |  |  | **92** |  |  |  |  |  |
| **28** | X | X |  |  |  | **93** |  |  |  |  |  |
| **29** | X | X |  |  |  | **94** |  |  |  |  |  |
| **30** | X | X |  |  |  | **95** |  |  |  |  |  |
| **31** | X | X |  |  |  | **96** |  |  |  |  |  |
| **32** | X | X |  |  |  | **97** |  |  |  |  |  |
| **33** | X | X |  |  |  | **98** |  |  |  |  |  |
| **34** | X | X |  |  |  | **99** |  |  |  |  |  |
| **35** | X | X |  |  |  | **100** |  |  |  |  |  |
| **36** | X | X |  |  |  | **101** |  |  |  |  |  |
| **37** | X | X |  |  |  | **102** |  |  |  |  |  |
| **38** | X | X |  |  |  | **103** |  |  |  |  |  |
| **39** | X | X |  |  |  | **104** |  |  |  |  |  |
| **40** | X | X |  |  |  | **105** |  |  |  |  |  |
| **41** | X | X |  |  |  | **106** |  |  |  |  |  |
| **42** | X | X |  |  |  | **107** |  |  |  |  |  |
| **43** | X | X |  |  |  | **108** |  |  |  |  |  |
| **44** | X | X |  |  |  | **109** |  |  |  |  |  |
| **45** | X | X |  |  |  | **110** |  |  |  |  |  |
| **46** | X | X |  |  |  | **111** |  |  |  |  |  |
| **47** | X | X |  |  |  | **112** |  |  |  |  |  |
| **48** | X | X |  |  |  | **113** |  |  |  |  |  |
| **49** | X | X |  |  |  | **114** |  |  |  |  |  |
| **50** | X | X |  |  |  | **115** |  |  |  |  |  |
| **51** | X | X |  |  |  | **116** |  |  |  |  |  |
| **52** | X | X |  |  |  | **117** |  |  |  |  |  |
| **53** |  | X |  |  |  | **118** |  |  |  |  |  |
| **54** |  | X |  |  |  | **119** |  |  |  |  |  |
| **55** |  | X |  |  |  | **120** |  |  |  |  |  |
| **56** |  | X |  |  |  | **121** |  |  |  |  |  |
| **57** |  | X |  |  |  | **122** |  |  |  |  |  |
| **58** |  | X |  |  |  | **123** |  |  |  |  |  |
| **59** |  | X |  |  |  | **124** |  |  |  |  |  |
| **60** |  | X |  |  |  | **125** |  |  |  |  |  |
| **61** |  | X |  |  |  | **126** |  |  |  |  |  |
| **62** |  | X |  |  |  | **127** |  |  |  |  |  |
| **63** |  | X |  |  |  | **128** |  |  |  |  |  |
| **64** |  |  |  |  |  | **129** |  |  |  |  |  |
| **65** |  |  |  |  |  | **130** |  |  |  |  |  |

**CONTENTS** *(general revised)*

D01

[1.0 INTRODUCTION 4](#_Toc108258727)

[2.0 Scope 4](#_Toc108258728)

[3.0 NORMATIVE REFERENCES 5](#_Toc108258729)

[3.1 Local Codes and Standards 5](#_Toc108258730)

[3.2 International Codes and Standards 5](#_Toc108258731)

[3.3 ENVIRONMENTAL DATA 5](#_Toc108258732)

[4.0 Site Conditions 6](#_Toc108258733)

[4.1 Site location 6](#_Toc108258734)

[4.2 External design conditions (for HVAC design calculation) 6](#_Toc108258735)

[5.0 Internal design conditions (Control Room Building) 7](#_Toc108258736)

[6.0 HVAC CALCULATION 8](#_Toc108258737)

[6.1 Design weather Parameters: 8](#_Toc108258738)

[6.2 CONSTRUCTIONS U-VALUE: 10](#_Toc108258739)

[6.3 SPACES INPUT DATA: 12](#_Toc108258740)

[6.4 Air System Inputs: 32](#_Toc108258741)

[6.5 Air System Information 34](#_Toc108258742)

[7.0 Equipment Selection 61](#_Toc108258743)

1. **INTRODUCTION**

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO).Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

**GENERAL DEFINITION**

The following terms shall be used in this document.

|  |  |
| --- | --- |
| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| PROJECT: | Binak Oilfield Development – General Facilities |
| GENERAL CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of :Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR(GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR |
| MAY: | Is used where a provision is completely discretionary. |

1. **Scope**

This document covers minimum necessary requirements for basis of design and main equipment’s to be used for the Heating, Ventilating, Air-Conditioning and pressurizing and plumbing system for buildings for project

1. **NORMATIVE REFERENCES**

## Local Codes and Standards

* IPS Iranian petroleum standards
* INBC Iranian National Building Code

## International Codes and Standards

* ASTM American Society for Testing Materials Relevant Parts
* API 610 Centrifugal Pumps for General Refinery Service, 10th Edition
* ISO 15156 Petroleum and Natural Gas Industries. Materials for use in H2S Containing Environments in Oil and Gas

Production

* AMCA Air Movement and Control Association
* ANSI American National Standards Institute.
* ASHRAE American Society of Heating, Refrigeration and Air-conditioning Engineer
* ASTM American Society for Testing and Material
* BOCA Building Officials and Code Administrators international
* BS British Standards
* CIBSE Chartered Institute of Building Services Engineers.
* NFPA National fire protection association
* SBCCI Southern Building Code Congress International
* SMACNA Sheet Metal and Air Conditioning Contractors’ National Association
* AWWA [American Water Works Association](http://www.awwa.org/)
* ASME [The American Society of Mechanical Engineers](https://www.asme.org/)

Note: The latest issued or revised edition of all above mentioned codes and standards shall be considered as reference.

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No BK-GNRAL-PEDCO-000-PR-DB-0001 .

1. **Site Conditions**

The following information is related to Bandar Deylam and Genaveh.

## Site location

* + Latitude 30° 32’ N
  + Longitude 50° 17’ E
  + Elevation 10 m

## External design conditions (for HVAC design calculation)

* + Summer dry bulb temperature : 41° C
  + Summer relative humidity : 61 %
  + Summer daily range temperature : 15.0° C
  + Winter dry bulb temperature : 6.0° C
  + Winter relative humidity : 100%

Note1: Outdoor refrigeration equipment shall be designed to maintain design conditions with an

50 °C temperature.

1. **Internal design conditions (Control Room Building)**

BASED ON “HVAC DESIGN CRITERIA” DOC. NUMBER: BK-GNRAL-PEDCO-000-HV-DC-0001

| **Room** | **Min. Fresh Air**  **(Note 3)** | **Min. Exhaust** | **Room Temp**  **Winter/Summer**  **(Deg C)** | **Relative Humidity**  **Winter/Summer**  **(Min/Max)%** | **Over Pressure Value (Pa)** | **Equipment Heat Gain**  **(Watts)** |
| --- | --- | --- | --- | --- | --- | --- |
| Control Room | 10% supply air | - | 22/24 | 30/60 | Positive | See( 13.3Design Criteria) |
| Engineering Room | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| Auxiliary Room | 10% supply air | - | 22/24 | 30/60 | Positive | See( 13.3Design Criteria) |
| UPS & Charger Room | 1 ACH | - | 22/24 | 30/60 | Positive | See( 13.3Design Criteria) |
| Toilet | - | 15 ACH | 20/26 | NC | Negative | - |
| Battery Room | 1 ACH | 10 ACH | 20/27±2 | 30/60 | Negative | - |
| Corridor | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| Air Lock | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| Office | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| Archive | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| HVAC Control Panel Room | 1 ACH | - | 10/30 | NC | Positive | - |
| Prayer Room | 10 l/s. person | - | 22/24 | 30/60 | - | - |
| Instrument Room | 10 l/s. person | - | 22/24 | 30/60 | Positive | - |
| Pantry | 10 l/s. person | 6 ACH | 22/24 | 30/60 | - | - |
| Locker & Shower | 2 ACH | 8 ACH | 20/26 | NC | Negative | - |

1. **HVAC CALCULATION**

## Design weather Parameters:

Design Parameters:

City Name …………………………………………………………………………**bink**

Location **IRAN**

Latitude **30.3** Deg. Longitude **-50.2** Deg. Elevation **10.0** m Summer Design Dry-Bulb **41.0** °C Summer Coincident Wet-Bulb **34.0** °C Summer Daily Range **15.0** °K Winter Design Dry-Bulb **6.0** °C Winter Design Wet-Bulb **6.0** °C Atmospheric Clearness Number **1.00** Average Ground Reflectance **0.20**

Soil Conductivity **1.385** W/(m-°K) Local Time Zone (GMT +/- N hours) **-1.0** hours Consider Daylight Savings Time **No** Simulation Weather Data **none N/A**

Current Data is **User Modified**

Design Cooling Months **January to December**

Design Day Maximum Solar Heat Gains

(The MSHG values are expressed in W/m² )

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Month** | **N** | **NNE** | **NE** | **ENE** | **E** | **ESE** | **SE** | **SSE** | **S** |
| January | 76.4 | 76.4 | 104.1 | 335.1 | 577.4 | 722.3 | 796.4 | 786.7 | 764.0 |
| February | 88.0 | 88.0 | 230.9 | 458.1 | 662.9 | 773.4 | 774.9 | 717.7 | 674.9 |
| March | 100.7 | 108.6 | 368.7 | 585.3 | 707.6 | 758.3 | 705.1 | 595.4 | 528.1 |
| April | 113.1 | 256.3 | 472.2 | 642.7 | 716.0 | 679.9 | 580.0 | 422.9 | 334.5 |
| May | 124.2 | 353.9 | 534.8 | 663.8 | 694.2 | 620.4 | 475.0 | 290.9 | 209.6 |
| June | 157.8 | 384.6 | 558.6 | 667.1 | 676.8 | 585.8 | 428.0 | 240.6 | 172.3 |
| July | 127.6 | 344.7 | 537.1 | 656.3 | 678.1 | 598.4 | 463.4 | 281.6 | 203.3 |
| August | 118.2 | 248.3 | 466.5 | 623.6 | 687.8 | 654.3 | 558.9 | 407.2 | 322.5 |
| September | 104.5 | 113.3 | 336.6 | 555.0 | 683.3 | 716.4 | 681.4 | 580.5 | 517.4 |
| October | 90.9 | 90.9 | 201.8 | 462.7 | 636.7 | 736.7 | 756.5 | 701.7 | 660.0 |
| November | 77.8 | 77.8 | 98.3 | 345.3 | 551.3 | 718.6 | 773.6 | 774.1 | 756.1 |
| December | 71.4 | 71.4 | 71.4 | 269.7 | 530.8 | 696.4 | 785.4 | 795.0 | 786.8 |
| **Month** | **SSW** | **SW** | **WSW** | **W** | **WNW** | **NW** | **NNW** | **HOR** | **Mult** |
| January | 789.5 | 796.9 | 721.1 | 569.2 | 354.1 | 83.2 | 76.4 | 579.3 | 1.00 |
| February | 722.0 | 781.4 | 766.3 | 669.5 | 467.5 | 224.5 | 88.0 | 702.0 | 1.00 |
| March | 596.6 | 704.4 | 761.1 | 720.6 | 569.4 | 368.1 | 116.6 | 809.9 | 1.00 |
| April | 421.4 | 576.3 | 689.2 | 714.5 | 631.4 | 476.0 | 257.9 | 863.7 | 1.00 |
| May | 289.5 | 470.8 | 624.0 | 691.1 | 655.0 | 542.6 | 355.7 | 877.6 | 1.00 |
| June | 238.3 | 421.9 | 590.9 | 670.1 | 656.4 | 565.4 | 389.3 | 873.7 | 1.00 |
| July | 278.1 | 456.2 | 609.2 | 671.7 | 644.3 | 540.2 | 353.4 | 863.9 | 1.00 |
| August | 405.5 | 554.8 | 664.2 | 689.2 | 610.9 | 463.3 | 256.0 | 845.0 | 1.00 |
| September | 580.7 | 681.6 | 714.0 | 684.8 | 554.4 | 333.4 | 114.2 | 785.9 | 1.00 |
| October | 698.5 | 750.4 | 744.7 | 624.3 | 458.7 | 216.5 | 90.9 | 693.3 | 1.00 |
| November | 770.3 | 775.6 | 718.6 | 559.7 | 335.4 | 103.0 | 77.8 | 579.1 | 1.00 |
| December | 796.5 | 774.3 | 701.4 | 517.9 | 296.9 | 71.4 | 71.4 | 527.6 | 1.00 |

## CONSTRUCTIONS U-VALUE:

**External Wall**

**Wall Details**

    Outside Surface Color   **Dark**

    Absorptivity   **0.900**

    Overall U-Value   **0.642** W/(m²-°K)

**Wall Layers Details (Inside to Outside)**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | **Thickness** | **Density** | **Specific Ht.** | **R-Value** | **Weight** |
| **Layers** | **mm** | **kg/m³** | **kJ / (kg - °K)** | **(m²-°K)/W** | **kg/m²** |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| concrete | 300.000 | 2242.6 | 0.84 | 0.17334 | 672.8 |
| insulation | 50.000 | 32.0 | 0.92 | 1.13000 | 1.6 |
| face brick | 100.000 | 2002.3 | 0.92 | 0.07504 | 200.2 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| **Totals** | **450.000** | **-** |  | **1.55766** | **874.6** |

**External Roof**

**Roof Details**

    Outside Surface Color   **Dark**

    Absorptivity   **0.900**

    Overall U-Value   **0.510** W/(m²-°K)

**Roof Layers Details (Inside to Outside)**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | **Thickness** | **Density** | **Specific Ht.** | **R-Value** | **Weight** |
| **Layers** | **mm** | **kg/m³** | **kJ / (kg - °K)** | **(m²-°K)/W** | **kg/m²** |
| Inside surface resistance | 0.000 | 0.0 | 0.00 | 0.12064 | 0.0 |
| concrete | 300.000 | 2242.6 | 0.84 | 0.17334 | 672.8 |
| board insulation | 50.000 | 32.0 | 0.92 | 1.13000 | 1.6 |
| cement mortar | 50.000 | 1121.3 | 1.47 | 0.40000 | 56.1 |
| Terrazzo | 20.000 | 608.7 | 0.84 | 0.08000 | 12.2 |
| Outside surface resistance | 0.000 | 0.0 | 0.00 | 0.05864 | 0.0 |
| **Totals** | **420.000** | **-** |  | **1.96262** | **742.6** |

**DOORS:**

**1\*2.5**

**Door Details:**

    Gross Area   **2.5** m²

    Door U-Value   **5.800** W/(m²-°K)

**Glass Details:**

    Glass Area   **0.0** m²

    Glass U-Value   **3.293** W/(m²-°K)

    Glass Shade Coefficient   **0.880**

    Glass Shaded All Day?   **No**

**1.5 x 2.5**

**Door Details:**

    Gross Area   **3.8** m²

    Door U-Value   **5.800** W/(m²-°K)

**Glass Details:**

    Glass Area   **0.0** m²

    Glass U-Value   **3.293** W/(m²-°K)

    Glass Shade Coefficient   **0.880**

    Glass Shaded All Day?   **No**

## SPACES INPUT DATA:

**AIR LOCK**

**1. General Details:**

    Floor Area   **3.2** m²

    Avg. Ceiling Height   **2.6** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **100** % of supply air

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **1.0** Person

    Activity Level   **User defined**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 7.2 | 0 | 0 | 1 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

    Door Type   **None**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 3.2 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **3.2** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **1.6** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**ARCHIVE**

**1. General Details:**

    Floor Area   **18.3** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.25**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **300.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 15.0 | 0 | 0 | 0 |
| S | 20.2 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

**3.2. Construction Types for Exposure S**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 18.3 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **18.3** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **8.2** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**BATTERY ROOM**

**1. General Details:**

    Floor Area   **57.6** m²

    Avg. Ceiling Height   **4.0** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **640.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.0** Watts

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **0.0** Person

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **None**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **2000.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 44.3 | 0 | 0 | 1 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

    Door Type   **1.2\*2.5**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 57.6 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **57.6** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **10.3** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**CONTROL ROOM**

**1. General Details:**

    Floor Area   **62.4** m²

    Avg. Ceiling Height   **3.2** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **100.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **5.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **750** W

    Schedule   **Equipment**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **4000.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

**(No Wall, Window, Door data).**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 62.4 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor Below Grade**

    Floor Area   **62.4** m²

    Exposed Perimeter   **0.0** m

    Total Floor U-Value   **2.000** W/(m²-°K)

    Floor Depth   **1.0** m

    Basement Wall U-Value   **0.568** W/(m²-°K)

    Wall Insulation R-Value   **0.00** (m²-°K)/W

    Wall Insulation Depth   **0.0** m

**7. Partitions:**

**(No partition data).**

**Corridor 1**

**1. General Details:**

    Floor Area   **34.8** m²

    Avg. Ceiling Height   **2.6** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **3.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 10.1 | 0 | 0 | 1 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

    Door Type   **1.2\*2.5**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 34.8 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **34.8** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **0.0** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**7.1. 1st Partition Details:**

    Partition Type   **Wall Partition**

    Area   **32.0** m²

    U-Value   **1.860** W/(m²-°K)

    Uncondit. Space Max Temp   **27.0** °C

    Ambient at Space Max Temp   **41.0** °C

    Uncondit. Space Min Temp   **10.0** °C

    Ambient at Space Min Temp   **6.0** °C

**7.2. 2nd Partition Details:**

    Partition Type   **Wall Partition**

    Area   **38.7** m²

    U-Value   **1.860** W/(m²-°K)

    Uncondit. Space Max Temp   **28.0** °C

    Ambient at Space Max Temp   **41.0** °C

    Uncondit. Space Min Temp   **22.0** °C

    Ambient at Space Min Temp   **6.0** °C

**Corridor 2**

**1. General Details:**

    Floor Area   **9.5** m²

    Avg. Ceiling Height   **2.6** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **1.0** Person

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

**(No Wall, Window, Door data).**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 9.5 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **9.5** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **0.0** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**7.1. 1st Partition Details:**

    Partition Type   **Wall Partition**

    Area   **20.0** m²

    U-Value   **1.860** W/(m²-°K)

    Uncondit. Space Max Temp   **26.0** °C

    Ambient at Space Max Temp   **41.0** °C

    Uncondit. Space Min Temp   **20.0** °C

    Ambient at Space Min Temp   **6.0** °C

**7.2. 2nd Partition Details:**

    Partition Type   **Wall Partition**

    Area   **38.7** m²

    U-Value   **1.860** W/(m²-°K)

    Uncondit. Space Max Temp   **28.0** °C

    Ambient at Space Max Temp   **41.0** °C

    Uncondit. Space Min Temp   **22.0** °C

    Ambient at Space Min Temp   **6.0** °C

**ENGINEERING ROOM**

**1. General Details:**

    Floor Area   **20.0** m²

    Avg. Ceiling Height   **3.2** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **3.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **450.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| N | 25.0 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure N**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 19.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor Below Grade**

    Floor Area   **20.0** m²

    Exposed Perimeter   **5.7** m

    Total Floor U-Value   **2.000** W/(m²-°K)

    Floor Depth   **1.0** m

    Basement Wall U-Value   **0.568** W/(m²-°K)

    Wall Insulation R-Value   **0.00** (m²-°K)/W

    Wall Insulation Depth   **0.0** m

**7. Partitions:**

**(No partition data).**

**hvac control panel**

**1. General Details:**

    Floor Area   **12.0** m²

    Avg. Ceiling Height   **3.2** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **3.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **2000.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 10.3 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 12.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **12.0** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **2.4** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**Instrument Room**

**1. General Details:**

    Floor Area   **20.1** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.25**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **300.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| E | 13.5 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure E**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 20.1 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **20.1** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **3.0** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**7.1. 1st Partition Details:**

    Partition Type   **Wall Partition**

    Area   **27.0** m²

    U-Value   **2.839** W/(m²-°K)

    Uncondit. Space Max Temp   **26.0** °C

    Ambient at Space Max Temp   **44.0** °C

    Uncondit. Space Min Temp   **20.0** °C

    Ambient at Space Min Temp   **6.0** °C

**7.2. 2nd Partition Details:**

**(No partition data).**

**ITR**

**1. General Details:**

    Floor Area   **90.7** m²

    Avg. Ceiling Height   **3.2** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10** % of supply air

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **20000.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| N | 27.0 | 0 | 0 | 1 |
| E | 62.0 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure N**

    Wall Type   **External Wall**

    Door Type   **1.5 x 2.5**

**3.2. Construction Types for Exposure E**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 90.7 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor Below Grade**

    Floor Area   **90.7** m²

    Exposed Perimeter   **20.7** m

    Total Floor U-Value   **2.000** W/(m²-°K)

    Floor Depth   **1.0** m

    Basement Wall U-Value   **0.568** W/(m²-°K)

    Wall Insulation R-Value   **0.00** (m²-°K)/W

    Wall Insulation Depth   **0.0** m

**7. Partitions:**

**(No partition data).**

**LOCKER AND SHOWER**

**1. General Details:**

    Floor Area   **20.0** m²

    Avg. Ceiling Height   **2.5** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **85.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **User defined**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| E | 13.8 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure E**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 20.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **20.0** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **3.2** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**OFFICE (1)**

**1. General Details:**

    Floor Area   **15.0** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.25**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **3.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **450.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 13.8 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 15.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **15.0** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **3.2** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**OFFICE (2)**

**1. General Details:**

    Floor Area   **10.8** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **10.0** L/s/person

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.25**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **300.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| W | 15.8 | 0 | 0 | 0 |
| S | 20.7 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure W**

    Wall Type   **External Wall**

**3.2. Construction Types for Exposure S**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 10.8 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** L/s

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **10.8** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **0.0** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**Pantry**

**1. General Details:**

    Floor Area   **23.6** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **133.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.0** Watts

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **5.0** People

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **1106** W

    Schedule   **Equipment**

    Latent   **574** W

    Schedule   **Equipment**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| S | 28.4 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure S**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 23.6 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **23.6** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **6.6** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**7.1. 1st Partition Details:**

    Partition Type   **Wall Partition**

    Area   **16.7** m²

    U-Value   **2.839** W/(m²-°K)

    Uncondit. Space Max Temp   **26.0** °C

    Ambient at Space Max Temp   **44.0** °C

    Uncondit. Space Min Temp   **20.0** °C

    Ambient at Space Min Temp   **6.0** °C

**7.2. 2nd Partition Details:**

**(No partition data)**

**Prayer Room**

**1. General Details:**

    Floor Area   **9.2** m²

    Avg. Ceiling Height   **2.5** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **30.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **3.0** People

    Activity Level   **User defined**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

**(No Wall, Window, Door data).**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 9.2 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **9.2** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **0.0** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**Toilet**

**1. General Details:**

    Floor Area   **34.0** m²

    Avg. Ceiling Height   **2.5** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **140.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **2.0** People

    Activity Level   **User defined**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| S | 27.0 | 0 | 0 | 0 |
| E | 23.0 | 0 | 0 | 0 |

**3.1. Construction Types for Exposure S**

    Wall Type   **External Wall**

**3.2. Construction Types for Exposure E**

    Wall Type   **External Wall**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 34.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **34.0** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **11.7** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

**UPS ROOM**

**1. General Details:**

    Floor Area   **23.0** m²

    Avg. Ceiling Height   **2.8** m

    Building Weight   **341.8** kg/m²

**1.1. OA Ventilation Requirements:**

    Space Usage   **User-Defined**

    OA Requirement 1   **20.0** L/s

    OA Requirement 2   **0.00** L/(s-m²)

    Space Usage Defaults   **ASHRAE Standard 62.1-2007**

**2. Internals:**

**2.1. Overhead Lighting:**

    Fixture Type   **Free Hanging**

    Wattage   **20.00** W/m²

    Ballast Multiplier   **1.20**

    Schedule   **Lighting**

**2.4. People:**

    Occupancy   **1.0** Person

    Activity Level   **Office Work**

    Sensible   **71.8** W/person

    Latent   **60.1** W/person

    Schedule   **People**

**2.2. Task Lighting:**

    Wattage   **0.00** W/m²

    Schedule   **None**

**2.5. Miscellaneous Loads:**

    Sensible   **0** W

    Schedule   **None**

    Latent   **0** W

    Schedule   **None**

**2.3. Electrical Equipment:**

    Wattage   **5000.0** Watts

    Schedule   **Equipment**

**3. Walls, Windows, Doors:**

| **Exp.** | **Wall Gross Area (m²)** | **Window 1 Qty.** | **Window 2 Qty.** | **Door 1 Qty.** |
| --- | --- | --- | --- | --- |
| N | 25.0 | 0 | 0 | 0 |
| W | 18.5 | 0 | 0 | 1 |

**3.1. Construction Types for Exposure N**

    Wall Type   **External Wall**

**3.2. Construction Types for Exposure W**

    Wall Type   **External Wall**

    Door Type   **1.2\*2.5**

**4. Roofs, Skylights:**

| **Exp.** | **Roof Gross Area (m²)** | **Roof Slope (deg.)** | **Skylight Qty.** |
| --- | --- | --- | --- |
| H | 22.0 | 0 | 0 |

**4.1. Construction Types for Exposure H**

    Roof Type   **External Roof**

**5. Infiltration:**

    Design Cooling   **0.00** ACH

    Design Heating   **0.00** L/s

    Energy Analysis   **0.00** L/s

    Infiltration occurs only when the fan is off.

**6. Floors:**

    Type   **Slab Floor On Grade**

    Floor Area   **23.0** m²

    Total Floor U-Value   **2.000** W/(m²-°K)

    Exposed Perimeter   **9.9** m

    Edge Insulation R-Value   **0.00** (m²-°K)/W

**7. Partitions:**

**(No partition data).**

## Air System Inputs:

**1. General Details:**

    Air System Name   **CONTROL BUILDING**

    Equipment Type   **Split AHU**

    Air System Type   **CAV with Terminal Reheat**

    Number of zones   **4**

**2. Ventilation System Components:**

**Ventilation Air Data:**

    Airflow Control   **Constant Ventilation Airflow**

    Ventilation Sizing Method   **Sum of Space OA Airflows**

    Unocc. Damper Position   **Closed**

    Damper Leak Rate   **0** %

    Outdoor Air CO2 Level   **400** ppm

**Central Cooling Data:**

    Supply Air Temperature   **14.0** °C

    Coil Bypass Factor   **0.100**

    Cooling Source   **Air-Cooled DX**

    Schedule   **JFMAMJJASOND**

    Capacity Control   **Cycled or Staged Capacity - Fan On**

**Supply Fan Data:**

    Fan Type   **Backward Inclined or Airfoil (BI/AF)**

    Configuration   **Draw-thru**

    Fan Performance   **1201** Pa

    Overall Efficiency   **60** %

**Duct System Data:**

**Supply Duct Data:**

    Duct Heat Gain   **0** %

    Duct Leakage   **0** %

**Return Duct or Plenum Data:**

    Return Air Via   **Ducted Return**

**3. Zone Components:**

**Space Assignments:**

|  |  |
| --- | --- |
| **Zone 1: Zone 1** |  |
| AIR LOCK | x1 |
| CONTROL ROOM | x1 |
| Corridor 1 | x1 |
| ENGINEERING ROOM | x1 |
| OFFICE (1) | x1 |
| OFFICE (2) | x1 |
| Pantry | x1 |
| Prayer Room | x1 |
| UPS ROOM | x1 |
| Corridor 2 | x1 |
| Instrument Room | x1 |
| ITR | x1 |
| ARCHIVE | x1 |
| **Zone 2: Zone 2** |  |
| BATTERY ROOM | x1 |
| **Zone 3: Zone 3** |  |
| LOCKER AND SHOWER | x1 |
| Toilet | x1 |
| **Zone 4: Zone 4** |  |
| hvac control panel | x1 |

**Thermostats and Zone Data:**

| **Zone** | **Cooling T-Stat Occ.** | **Cooling T-Stat Unocc.** | **Heating T-Stat Occ.** | **Heating T-Stat Unocc.** | **T-Stat Throttling Range** | **Diversity Factor** | **Direct Exhaust Airflow** | **Direct Exhaust Fan** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | **(°C)** | **(°C)** | **(°C)** | **(°C)** | **(°C)** | **(%)** | **(L/s)** | **(kW)** |
| **1** | 24.0 | 24.0 | 22.0 | 22.0 | 0.83 | 100 | 0.0 | 0.0 | |
| **2** | 27.0 | 27.0 | 20.0 | 20.0 | 0.83 | 100 | 0.0 | 0.0 | |
| **3** | 26.0 | 26.0 | 20.0 | 20.0 | 0.83 | 100 | 0.0 | 0.0 | |
| **4** | 27.0 | 27.0 | 10.0 | 10.0 | 0.83 | 100 | 0.0 | 0.0 | |

    Thermostat Schedule   **Fan**

    Unoccupied Cooling is   **Available**

**Supply Terminals Data:**

    Zone   **All**

    Terminal Type   **Diffuser with RH**

    Minimum Airflow   **0.00** L/s/person

    Reheat Coil Source   **Electric Resistance**

    Reheat Coil Schedule   **JFMAMJJASOND**

**Zone Heating Units:**

    Zone   **All**

    Zone Heating Unit Type   **None**

    Zone Unit Heat Source   **Electric Resistance**

    Zone Heating Unit Schedule   **JFMAMJJASOND**

**4. Sizing Data (Computer-Generated):**

**System Sizing Data:**

**Sizing Data:**

    Cooling Supply Temperature   **14.0** °C

    Supply Fan Airflow   **5738.8** L/s

    Ventilation Airflow   **1580.3** L/s

**Hydronic Sizing Specifications:**

    Chilled Water Delta-T   **5.6** °K

    Hot Water Delta-T   **11.1** °K

**Safety Factors:**

    Cooling Sensible   **10** %

    Cooling Latent   **10** %

    Heating   **10** %

**Zone Sizing Data:**

    Zone Airflow Sizing Method   **Sum of space airflow rates**

    Space Airflow Sizing Method   **Individual peak space loads**

| **Zone** | **Supply Airflow** | **Zone Htg Unit** | **Reheat Coil** | **-** |
| --- | --- | --- | --- | --- |
|  | **(L/s)** | **(kW)** | **(kW)** | **-** |
| **1** | 4681.2 | - | 54.9 | - | |
| **2** | 640.0 | - | 5.9 | - | |
| **3** | 225.0 | - | 2.9 |  | |
| **4** | 192.6 | - | 0.1 |  | |

**5. Equipment Data**

**Central Cooling Unit - Air-Cooled DX**

    Design OAT   **35.0** °C

    Equipment Sizing   **Auto-Sized**

    Capacity Oversizing Factor   **0** %

    ARI Performance Rating   **3.224** EER

    Conventional Cutoff OAT   **12.8** °C

    Low Temperature Operation   **Used**

    Low Temperature Cutoff OAT   **-17.8** °C

## Air System Information

    Air System Name   **CONTROL BUILDING**

    Equipment Class   **SPLT AHU**

    Air System Type   **CAV/RH**

Number of zones   **4**

Floor Area   **464.2** m²

Location   **binak, IRAN**

**Sizing Calculation Information**

    Calculation Months   **Jan to Dec**

    Sizing Data   **Calculated**

Zone L/s Sizing   **Sum of space airflow rates**

Space L/s Sizing   **Individual peak space loads**

**Central Cooling Coil Sizing Data**

    Total coil load   **217.4** kW

    Sensible coil load   **110.0** kW

    Coil L/s at Jul 1500   **5750** L/s

    Max block L/s   **5750** L/s

    Sum of peak zone L/s   **5750** L/s

    Sensible heat ratio   **0.506**

    m²/kW   **2.1**

    W/m²   **468.3**

    Water flow @ 5.6 °K rise   **N/A**

Load occurs at   **Jul 1500**

OA DB / WB   **41.0 / 34.0** °C

Entering DB / WB   **28.8 / 23.0** °C

Leaving DB / WB   **12.9 / 12.6** °C

Coil ADP   **11.1** °C

Bypass Factor   **0.100**

Resulting RH   **49** %

Design supply temp.   **14.0** °C

Zone T-stat Check   **4 of 4** OK

Max zone temperature deviation   **0.0** °K

**Supply Fan Sizing Data**

    Actual max L/s   **5750** L/s

    Standard L/s   **5743** L/s

    Actual max L/(s-m²)   **12.39** L/(s-m²)

Fan motor BHP   **14.51** BHP

Fan motor kW   **11.51** kW

Fan static   **1201** Pa

**Outdoor Ventilation Air Data**

    Design airflow L/s   **1586** L/s

    L/(s-m²)   **3.42** L/(s-m²)

L/s/person   **39.64** L/s/person

**Air System Information**

    Air System Name   **CONTROL BUILDING**

    Equipment Class   **SPLT AHU**

    Air System Type   **CAV/RH**

Number of zones   **4**

Floor Area   **464.2** m²

Location   **binak, IRAN**

**Sizing Calculation Information**

    Calculation Months   **Jan to Dec**

    Sizing Data   **Calculated**

Zone L/s Sizing   **Sum of space airflow rates**

Space L/s Sizing   **Individual peak space loads**

**Zone Sizing Data**

|  | **Maximum** |  |  |  | **Maximum** | **Zone** |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | **Cooling** | **Design** | **Minimum** |  | **Heating** | **Floor** |  |
|  | **Sensible** | **Airflow** | **Airflow** | **Time of** | **Load** | **Area** | **Zone** |
| **Zone Name** | **(kW)** | **(L/s)** | **(L/s)** | **Peak Load** | **(kW)** | **(m²)** | **L/(s-m²)** |
| Zone 1 | 56.2 | 4693 | 4693 | Jul 1700 | 9.9 | 340.6 | 13.78 |
| Zone 2 | 3.5 | 640 | 640 | Jul 1900 | 1.3 | 57.6 | 11.11 |
| Zone 3 | 3.1 | 225 | 225 | Jul 0000 | 1.3 | 54.0 | 4.17 |
| Zone 4 | 3.0 | 192 | 192 | Jul 0100 | 0.1 | 12.0 | 16.01 |

**Zone Terminal Sizing Data**

|  |  | **Reheat** | **Zone** | **Zone** |  |
| --- | --- | --- | --- | --- | --- |
|  | **Reheat** | **Coil** | **Htg** | **Htg** | **Mixing** |
|  | **Coil** | **Water** | **Coil** | **Water** | **Box Fan** |
|  | **Load** | **L/s** | **Load** | **L/s** | **Airflow** |
| **Zone Name** | **(kW)** | **@ 11.1 °K** | **(kW)** | **@ 11.1 °K** | **(L/s)** |
| Zone 1 | 55.2 | - | 0.0 | - | 0 |
| Zone 2 | 6.0 | - | 0.0 | - | 0 |
| Zone 3 | 2.9 | - | 0.0 | - | 0 |
| Zone 4 | 0.1 | - | 0.0 | - | 0 |

**Space Loads and Airflows**

|  |  | **Cooling** | **Time** | **Air** | **Heating** | **Floor** |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **Zone Name /** |  | **Sensible** | **of** | **Flow** | **Load** | **Area** | **Space** |
| **Space Name** | **Mult.** | **(kW)** | **Load** | **(L/s)** | **(kW)** | **(m²)** | **L/(s-m²)** |
| ***Zone 1*** |  |  |  |  |  |  |  |
| AIR LOCK | 1 | 0.5 | Jul 1500 | 44 | 0.4 | 3.2 | 13.60 |
| CONTROL ROOM | 1 | 8.1 | Jul 0100 | 672 | 0.6 | 62.4 | 10.77 |
| Corridor 1 | 1 | 2.3 | Jul 1500 | 192 | 1.5 | 34.8 | 5.53 |
| ENGINEERING ROOM | 1 | 1.8 | Jun 0100 | 145 | 0.6 | 20.0 | 7.27 |
| OFFICE (1) | 1 | 1.5 | Jul 0100 | 127 | 0.4 | 15.0 | 8.47 |
| OFFICE (2) | 1 | 1.4 | Aug 0100 | 113 | 0.5 | 10.8 | 10.48 |
| Pantry | 1 | 2.3 | Aug 1800 | 188 | 0.8 | 23.6 | 7.95 |
| Prayer Room | 1 | 0.6 | Jul 0100 | 50 | 0.1 | 9.2 | 5.44 |
| UPS ROOM | 1 | 7.1 | Jul 1600 | 591 | 1.1 | 23.0 | 25.70 |
| Corridor 2 | 1 | 0.8 | Jul 1500 | 65 | 0.2 | 9.5 | 6.87 |
| Instrument Room | 1 | 1.5 | Jul 1600 | 128 | 0.6 | 20.1 | 6.39 |
| ITR | 1 | 27.0 | Jul 1800 | 2240 | 2.6 | 90.7 | 24.70 |
| ARCHIVE | 1 | 1.6 | Aug 0100 | 137 | 0.7 | 18.3 | 7.47 |
| ***Zone 2*** |  |  |  |  |  |  |  |
| BATTERY ROOM | 1 | 3.5 | Jul 1900 | 640 | 1.3 | 57.6 | 11.11 |
| ***Zone 3*** |  |  |  |  |  |  |  |
| LOCKER AND SHOWER | 1 | 1.1 | Jul 0000 | 85 | 0.4 | 20.0 | 4.25 |
| Toilet | 1 | 2.0 | Aug 0000 | 140 | 0.9 | 34.0 | 4.12 |
| ***Zone 4*** |  |  |  |  |  |  |  |
| hvac control panel | 1 | 3.0 | Jul 0100 | 192 | 0.1 | 12.0 | 16.01 |

**1. Summary**

    Ventilation Sizing Method   **Sum of Space OA Airflows**

    Design Ventilation Airflow Rate   **1586** L/s

**2. Space Ventilation Analysis Table**

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | **Floor** |  | **Maximum** | **Required** | **Required** | **Required** | **Required** | **Uncorrected** |
|  |  | **Area** | **Maximum** | **Supply Air** | **Outdoor Air** | **Outdoor Air** | **Outdoor Air** | **Outdoor Air** | **Outdoor Air** |
| **Zone Name / Space Name** | **Mult.** | **(m²)** | **Occupants** | **(L/s)** | **(L/s/person)** | **(L/(s-m²))** | **(L/s)** | **(% of supply)** | **(L/s)** |
| **Zone 1** |  |  |  |  |  |  |  |  |  |
| AIR LOCK | 1 | 3.2 | 1.0 | 43.5 | 0.00 | 0.00 | 0.0 | 100.0 | 43.5 |
| CONTROL ROOM | 1 | 62.4 | 5.0 | 672.0 | 0.00 | 0.00 | 100.0 | 0.0 | 100.0 |
| Corridor 1 | 1 | 34.8 | 3.0 | 192.4 | 10.00 | 0.00 | 0.0 | 0.0 | 30.0 |
| ENGINEERING ROOM | 1 | 20.0 | 3.0 | 145.5 | 10.00 | 0.00 | 0.0 | 0.0 | 30.0 |
| OFFICE (1) | 1 | 15.0 | 3.0 | 127.1 | 10.00 | 0.00 | 0.0 | 0.0 | 30.0 |
| OFFICE (2) | 1 | 10.8 | 2.0 | 113.2 | 10.00 | 0.00 | 0.0 | 0.0 | 20.0 |
| Pantry | 1 | 23.6 | 5.0 | 187.7 | 0.00 | 0.00 | 133.0 | 0.0 | 133.0 |
| Prayer Room | 1 | 9.2 | 3.0 | 50.0 | 0.00 | 0.00 | 30.0 | 0.0 | 30.0 |
| UPS ROOM | 1 | 23.0 | 1.0 | 591.0 | 0.00 | 0.00 | 20.0 | 0.0 | 20.0 |
| Corridor 2 | 1 | 9.5 | 1.0 | 65.2 | 10.00 | 0.00 | 0.0 | 0.0 | 10.0 |
| Instrument Room | 1 | 20.1 | 2.0 | 128.5 | 10.00 | 0.00 | 0.0 | 0.0 | 20.0 |
| ITR | 1 | 90.7 | 2.0 | 2240.1 | 0.00 | 0.00 | 0.0 | 10.0 | 224.0 |
| ARCHIVE | 1 | 18.3 | 2.0 | 136.8 | 10.00 | 0.00 | 0.0 | 0.0 | 20.0 |
| **Zone 2** |  |  |  |  |  |  |  |  |  |
| BATTERY ROOM | 1 | 57.6 | 0.0 | 640.0 | 0.00 | 0.00 | 640.0 | 0.0 | 640.0 |
| **Zone 3** |  |  |  |  |  |  |  |  |  |
| LOCKER AND SHOWER | 1 | 20.0 | 2.0 | 85.0 | 0.00 | 0.00 | 85.0 | 0.0 | 85.0 |
| Toilet | 1 | 34.0 | 2.0 | 140.0 | 0.00 | 0.00 | 140.0 | 0.0 | 140.0 |
| **Zone 4** |  |  |  |  |  |  |  |  |  |
| hvac control panel | 1 | 12.0 | 3.0 | 192.2 | 0.00 | 0.00 | 10.0 | 0.0 | 10.0 |
| **Totals (incl. Space Multipliers)** |  |  |  | **5750.2** |  |  |  |  | **1585.5** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1500** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 41.0 °C / 34.0 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **ZONE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 405 m² | 3805 | - | 405 m² | 3944 | - |
| Roof Transmission | 462 m² | 4854 | - | 462 m² | 3581 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 16 m² | 1259 | - | 16 m² | 1431 | - |
| Floor Transmission | 464 m² | 0 | - | 464 m² | 1452 | - |
| Partitions | 173 m² | 804 | - | 173 m² | 1037 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 9304 W | 9304 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 34800 W | 34798 | - | 0 | 0 | - |
| People | 40 | 2872 | 2403 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 1856 | 574 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 5955 | 298 | 10% | 1144 | 0 |
| **>> Total Zone Loads** | **-** | **65508** | **3275** | **-** | **12589** | **0** |
| Zone Conditioning | - | 66036 | 3275 | - | 12314 | 0 |
| Plenum Wall Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Roof Load | 0% | 0 | - | 0 | 0 | - |
| Plenum Lighting Load | 0% | 0 | - | 0 | 0 | - |
| Return Fan Load | 5750 L/s | 0 | - | 5750 L/s | 0 | - |
| Ventilation Load | 1586 L/s | 32279 | 104082 | 1586 L/s | 29043 | 0 |
| Supply Fan Load | 5750 L/s | 11510 | - | 5750 L/s | -11510 | - |
| Space Fan Coil Fans | - | 0 | - | - | 0 | - |
| Duct Heat Gain / Loss | 0% | 0 | - | 0% | 0 | - |
| **>> Total System Loads** | **-** | **109825** | **107357** | **-** | **29847** | **0** |
| Central Cooling Coil | - | 110034 | 107358 | - | 0 | 0 |
| Terminal Reheat Coils | - | -208 | - | - | 29759 | - |
| **>> Total Conditioning** | **-** | **109825** | **107358** | **-** | **29759** | **0** |
| **Key:** | **Positive values are clg loads** | | | **Positive values are htg loads** | | |
|  | **Negative values are htg loads** | | | **Negative values are clg loads** | | |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Zone 1** | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1700** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 39.5 °C / 33.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **ZONE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 289 m² | 2828 | - | 289 m² | 2973 | - |
| Roof Transmission | 339 m² | 3786 | - | 339 m² | 2760 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 13 m² | 1011 | - | 13 m² | 1188 | - |
| Floor Transmission | 341 m² | 0 | - | 341 m² | 1046 | - |
| Partitions | 173 m² | 750 | - | 173 m² | 1037 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 7696 W | 7696 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 30800 W | 30799 | - | 0 | 0 | - |
| People | 33 | 2369 | 1983 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 1856 | 574 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 5110 | 256 | 10% | 900 | 0 |
| **>> Total Zone Loads** | **-** | **56205** | **2812** | **-** | **9904** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Zone 2** | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1900** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 35.9 °C / 33.1 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 27.0 °C** | | | **OCCUPIED T-STAT 20.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **ZONE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 41 m² | 388 | - | 41 m² | 371 | - |
| Roof Transmission | 58 m² | 580 | - | 58 m² | 411 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 3 m² | 146 | - | 3 m² | 244 | - |
| Floor Transmission | 58 m² | 0 | - | 58 m² | 178 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 24 W | 24 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2000 W | 2000 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 314 | 0 | 10% | 120 | 0 |
| **>> Total Zone Loads** | **-** | **3451** | **0** | **-** | **1324** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Zone 3** | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0000** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.7 °C / 28.4 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 26.0 °C** | | | **OCCUPIED T-STAT 20.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **ZONE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 64 m² | 599 | - | 64 m² | 573 | - |
| Roof Transmission | 54 m² | 603 | - | 54 m² | 385 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 54 m² | 0 | - | 54 m² | 217 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 1296 W | 1296 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 4 | 287 | 240 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 278 | 24 | 10% | 118 | 0 |
| **>> Total Zone Loads** | **-** | **3063** | **264** | **-** | **1293** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Zone 4** | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 27.0 °C** | | | **OCCUPIED T-STAT 10.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **ZONE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 10 m² | 107 | - | 10 m² | 26 | - |
| Roof Transmission | 12 m² | 128 | - | 12 m² | 24 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 12 m² | 0 | - | 12 m² | 11 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 288 W | 288 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2000 W | 2000 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 274 | 18 | 10% | 6 | 0 |
| **>> Total Zone Loads** | **-** | **3012** | **198** | **-** | **69** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.1.A. COMPONENT LOADS FOR SPACE '' AIR LOCK '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1500** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 41.0 °C / 34.0 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 4 m² | 45 | - | 4 m² | 43 | - |
| Roof Transmission | 3 m² | 35 | - | 3 m² | 26 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 3 m² | 249 | - | 3 m² | 278 | - |
| Floor Transmission | 3 m² | 0 | - | 3 m² | 21 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 77 W | 77 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 1 | 72 | 60 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 48 | 6 | 10% | 37 | 0 |
| **>> Total Zone Loads** | **-** | **525** | **66** | **-** | **406** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.1.B. ENVELOPE LOADS FOR SPACE '' AIR LOCK '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 4 | 0.642 | - | 45 | - | 43 |
| DOOR | 3 | 5.800 | - | 249 | - | 278 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 3 | 0.510 | - | 35 | - | 26 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.2.A. COMPONENT LOADS FOR SPACE '' CONTROL ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Roof Transmission | 62 m² | 760 | - | 62 m² | 509 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 62 m² | 0 | - | 62 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 1498 W | 1497 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 4000 W | 4000 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 750 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 737 | 30 | 10% | 51 | 0 |
| **>> Total Zone Loads** | **-** | **8103** | **330** | **-** | **560** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.2.B. ENVELOPE LOADS FOR SPACE '' CONTROL ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 62 | 0.510 | - | 760 | - | 509 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.3.A. COMPONENT LOADS FOR SPACE '' Corridor 1 '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1500** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 41.0 °C / 34.0 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 7 m² | 76 | - | 7 m² | 73 | - |
| Roof Transmission | 35 m² | 378 | - | 35 m² | 284 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 3 m² | 249 | - | 3 m² | 278 | - |
| Floor Transmission | 35 m² | 0 | - | 35 m² | 0 | - |
| Partitions | 71 m² | 356 | - | 71 m² | 714 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 835 W | 835 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 211 | 18 | 10% | 135 | 0 |
| **>> Total Zone Loads** | **-** | **2320** | **198** | **-** | **1484** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.3.B. ENVELOPE LOADS FOR SPACE '' Corridor 1 '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 7 | 0.642 | - | 76 | - | 73 |
| DOOR | 3 | 5.800 | - | 249 | - | 278 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 35 | 0.510 | - | 378 | - | 284 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.4.A. COMPONENT LOADS FOR SPACE '' ENGINEERING ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jun 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 27.4 °C / 27.1 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 25 m² | 218 | - | 25 m² | 257 | - |
| Roof Transmission | 19 m² | 231 | - | 19 m² | 155 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 20 m² | 0 | - | 20 m² | 110 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 480 W | 480 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 450 W | 450 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 159 | 18 | 10% | 52 | 0 |
| **>> Total Zone Loads** | **-** | **1754** | **198** | **-** | **574** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.4.B. ENVELOPE LOADS FOR SPACE '' ENGINEERING ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **N EXPOSURE** |  |  |  |  |  |  |
| WALL | 25 | 0.642 | - | 218 | - | 257 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 19 | 0.510 | - | 231 | - | 155 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.5.A. COMPONENT LOADS FOR SPACE '' OFFICE (1) '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 14 m² | 170 | - | 14 m² | 142 | - |
| Roof Transmission | 15 m² | 183 | - | 15 m² | 122 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 15 m² | 0 | - | 15 m² | 60 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 375 W | 375 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 450 W | 450 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 139 | 18 | 10% | 32 | 0 |
| **>> Total Zone Loads** | **-** | **1533** | **198** | **-** | **356** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.5.B. ENVELOPE LOADS FOR SPACE '' OFFICE (1) '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 14 | 0.642 | - | 170 | - | 142 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 15 | 0.510 | - | 183 | - | 122 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.6.A. COMPONENT LOADS FOR SPACE '' OFFICE (2) '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Aug 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 37 m² | 403 | - | 37 m² | 375 | - |
| Roof Transmission | 11 m² | 124 | - | 11 m² | 88 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 11 m² | 0 | - | 11 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 270 W | 270 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 300 W | 300 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 124 | 12 | 10% | 46 | 0 |
| **>> Total Zone Loads** | **-** | **1364** | **132** | **-** | **509** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.6.B. ENVELOPE LOADS FOR SPACE '' OFFICE (2) '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 16 | 0.642 | - | 191 | - | 162 |
| **S EXPOSURE** |  |  |  |  |  |  |
| WALL | 21 | 0.642 | - | 212 | - | 213 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 11 | 0.510 | - | 124 | - | 88 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.7.A. COMPONENT LOADS FOR SPACE '' Pantry '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Aug 1800** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 37.9 °C / 33.4 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 28 m² | 275 | - | 28 m² | 292 | - |
| Roof Transmission | 24 m² | 254 | - | 24 m² | 192 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 24 m² | 0 | - | 24 m² | 111 | - |
| Partitions | 17 m² | 40 | - | 17 m² | 95 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 24 W | 24 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 5 | 359 | 300 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 1106 | 574 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 206 | 87 | 10% | 69 | 0 |
| **>> Total Zone Loads** | **-** | **2263** | **962** | **-** | **759** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.7.B. ENVELOPE LOADS FOR SPACE '' Pantry '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **S EXPOSURE** |  |  |  |  |  |  |
| WALL | 28 | 0.642 | - | 275 | - | 292 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 24 | 0.510 | - | 254 | - | 192 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.8.A. COMPONENT LOADS FOR SPACE '' Prayer Room '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Roof Transmission | 9 m² | 112 | - | 9 m² | 75 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 9 m² | 0 | - | 9 m² | 0 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 221 W | 221 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 55 | 18 | 10% | 8 | 0 |
| **>> Total Zone Loads** | **-** | **603** | **198** | **-** | **83** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.8.B. ENVELOPE LOADS FOR SPACE '' Prayer Room '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 9 | 0.510 | - | 112 | - | 75 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.9.A. COMPONENT LOADS FOR SPACE '' UPS ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1600** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 40.6 °C / 33.9 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 41 m² | 366 | - | 41 m² | 416 | - |
| Roof Transmission | 22 m² | 242 | - | 22 m² | 179 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 3 m² | 247 | - | 3 m² | 278 | - |
| Floor Transmission | 23 m² | 0 | - | 23 m² | 140 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 552 W | 552 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 5000 W | 5000 | - | 0 | 0 | - |
| People | 1 | 72 | 60 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 648 | 6 | 10% | 101 | 0 |
| **>> Total Zone Loads** | **-** | **7126** | **66** | **-** | **1115** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.9.B. ENVELOPE LOADS FOR SPACE '' UPS ROOM '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **N EXPOSURE** |  |  |  |  |  |  |
| WALL | 25 | 0.642 | - | 200 | - | 257 |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 16 | 0.642 | - | 166 | - | 159 |
| DOOR | 3 | 5.800 | - | 247 | - | 278 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 22 | 0.510 | - | 242 | - | 179 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.10.A. COMPONENT LOADS FOR SPACE '' Corridor 2 '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1500** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 41.0 °C / 34.0 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Roof Transmission | 10 m² | 103 | - | 10 m² | 77 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 10 m² | 0 | - | 10 m² | 0 | - |
| Partitions | 59 m² | 312 | - | 59 m² | 74 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 228 W | 228 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 1 | 72 | 60 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 71 | 6 | 10% | 15 | 0 |
| **>> Total Zone Loads** | **-** | **786** | **66** | **-** | **167** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.10.B. ENVELOPE LOADS FOR SPACE '' Corridor 2 '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 10 | 0.510 | - | 103 | - | 77 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.11.A. COMPONENT LOADS FOR SPACE '' Instrument Room '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1600** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 40.6 °C / 33.9 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 14 m² | 158 | - | 14 m² | 139 | - |
| Roof Transmission | 20 m² | 221 | - | 20 m² | 164 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 20 m² | 0 | - | 20 m² | 63 | - |
| Partitions | 27 m² | 83 | - | 27 m² | 153 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 503 W | 502 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 300 W | 300 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 141 | 12 | 10% | 52 | 0 |
| **>> Total Zone Loads** | **-** | **1549** | **132** | **-** | **571** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.11.B. ENVELOPE LOADS FOR SPACE '' Instrument Room '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **E EXPOSURE** |  |  |  |  |  |  |
| WALL | 14 | 0.642 | - | 158 | - | 139 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 20 | 0.510 | - | 221 | - | 164 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.12.A. COMPONENT LOADS FOR SPACE '' ITR '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1800** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 37.9 °C / 33.4 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 85 m² | 925 | - | 85 m² | 875 | - |
| Roof Transmission | 91 m² | 1033 | - | 91 m² | 739 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 4 m² | 278 | - | 4 m² | 353 | - |
| Floor Transmission | 91 m² | 0 | - | 91 m² | 427 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 2177 W | 2177 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 20000 W | 19999 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 2455 | 12 | 10% | 239 | 0 |
| **>> Total Zone Loads** | **-** | **27010** | **132** | **-** | **2633** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.12.B. ENVELOPE LOADS FOR SPACE '' ITR '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **N EXPOSURE** |  |  |  |  |  |  |
| WALL | 23 | 0.642 | - | 188 | - | 238 |
| DOOR | 4 | 5.800 | - | 278 | - | 353 |
| **E EXPOSURE** |  |  |  |  |  |  |
| WALL | 62 | 0.642 | - | 736 | - | 637 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 91 | 0.510 | - | 1033 | - | 739 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.13.A. COMPONENT LOADS FOR SPACE '' ARCHIVE '' IN ZONE '' Zone 1 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Aug 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 24.0 °C** | | | **OCCUPIED T-STAT 22.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 35 m² | 388 | - | 35 m² | 362 | - |
| Roof Transmission | 18 m² | 210 | - | 18 m² | 149 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 18 m² | 0 | - | 18 m² | 114 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 458 W | 457 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 300 W | 300 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 150 | 12 | 10% | 62 | 0 |
| **>> Total Zone Loads** | **-** | **1649** | **132** | **-** | **687** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 1.13.B. ENVELOPE LOADS FOR SPACE '' ARCHIVE '' IN ZONE '' Zone 1 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 15 | 0.642 | - | 181 | - | 154 |
| **S EXPOSURE** |  |  |  |  |  |  |
| WALL | 20 | 0.642 | - | 207 | - | 207 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 18 | 0.510 | - | 210 | - | 149 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 2.1.A. COMPONENT LOADS FOR SPACE '' BATTERY ROOM '' IN ZONE '' Zone 2 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 1900** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 35.9 °C / 33.1 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 27.0 °C** | | | **OCCUPIED T-STAT 20.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 41 m² | 388 | - | 41 m² | 371 | - |
| Roof Transmission | 58 m² | 580 | - | 58 m² | 411 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 3 m² | 146 | - | 3 m² | 244 | - |
| Floor Transmission | 58 m² | 0 | - | 58 m² | 178 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 24 W | 24 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2000 W | 2000 | - | 0 | 0 | - |
| People | 0 | 0 | 0 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 314 | 0 | 10% | 120 | 0 |
| **>> Total Zone Loads** | **-** | **3451** | **0** | **-** | **1324** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 2.1.B. ENVELOPE LOADS FOR SPACE '' BATTERY ROOM '' IN ZONE '' Zone 2 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 41 | 0.642 | - | 388 | - | 371 |
| DOOR | 3 | 5.800 | - | 146 | - | 244 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 58 | 0.510 | - | 580 | - | 411 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 3.1.A. COMPONENT LOADS FOR SPACE '' LOCKER AND SHOWER '' IN ZONE '' Zone 3 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0000** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.7 °C / 28.4 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 26.0 °C** | | | **OCCUPIED T-STAT 20.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 14 m² | 148 | - | 14 m² | 124 | - |
| Roof Transmission | 20 m² | 223 | - | 20 m² | 143 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 20 m² | 0 | - | 20 m² | 57 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 480 W | 480 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 99 | 12 | 10% | 32 | 0 |
| **>> Total Zone Loads** | **-** | **1094** | **132** | **-** | **357** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 3.1.B. ENVELOPE LOADS FOR SPACE '' LOCKER AND SHOWER '' IN ZONE '' Zone 3 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **E EXPOSURE** |  |  |  |  |  |  |
| WALL | 14 | 0.642 | - | 148 | - | 124 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 20 | 0.510 | - | 223 | - | 143 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 3.2.A. COMPONENT LOADS FOR SPACE '' Toilet '' IN ZONE '' Zone 3 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Aug 0000** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.7 °C / 28.4 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 26.0 °C** | | | **OCCUPIED T-STAT 20.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 50 m² | 478 | - | 50 m² | 449 | - |
| Roof Transmission | 34 m² | 356 | - | 34 m² | 243 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 34 m² | 0 | - | 34 m² | 159 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 816 W | 816 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 0 W | 0 | - | 0 | 0 | - |
| People | 2 | 144 | 120 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 179 | 12 | 10% | 85 | 0 |
| **>> Total Zone Loads** | **-** | **1974** | **132** | **-** | **936** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 3.2.B. ENVELOPE LOADS FOR SPACE '' Toilet '' IN ZONE '' Zone 3 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **S EXPOSURE** |  |  |  |  |  |  |
| WALL | 27 | 0.642 | - | 241 | - | 243 |
| **E EXPOSURE** |  |  |  |  |  |  |
| WALL | 23 | 0.642 | - | 237 | - | 207 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 34 | 0.510 | - | 356 | - | 243 |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 4.1.A. COMPONENT LOADS FOR SPACE '' hvac control panel '' IN ZONE '' Zone 4 ''** | | | | | | |
|  | **DESIGN COOLING** | | | **DESIGN HEATING** | | |
|  | **COOLING DATA AT Jul 0100** | | | **HEATING DATA AT DES HTG** | | |
|  | **COOLING OA DB / WB 28.0 °C / 27.7 °C** | | | **HEATING OA DB / WB 6.0 °C / 6.0 °C** | | |
|  | **OCCUPIED T-STAT 27.0 °C** | | | **OCCUPIED T-STAT 10.0 °C** | | |
|  |  | **Sensible** | **Latent** |  | **Sensible** | **Latent** |
| **SPACE LOADS** | **Details** | **(W)** | **(W)** | **Details** | **(W)** | **(W)** |
| Window & Skylight Solar Loads | 0 m² | 0 | - | 0 m² | - | - |
| Wall Transmission | 10 m² | 107 | - | 10 m² | 26 | - |
| Roof Transmission | 12 m² | 128 | - | 12 m² | 24 | - |
| Window Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Skylight Transmission | 0 m² | 0 | - | 0 m² | 0 | - |
| Door Loads | 0 m² | 0 | - | 0 m² | 0 | - |
| Floor Transmission | 12 m² | 0 | - | 12 m² | 11 | - |
| Partitions | 0 m² | 0 | - | 0 m² | 0 | - |
| Ceiling | 0 m² | 0 | - | 0 m² | 0 | - |
| Overhead Lighting | 288 W | 288 | - | 0 | 0 | - |
| Task Lighting | 0 W | 0 | - | 0 | 0 | - |
| Electric Equipment | 2000 W | 2000 | - | 0 | 0 | - |
| People | 3 | 215 | 180 | 0 | 0 | 0 |
| Infiltration | - | 0 | 0 | - | 0 | 0 |
| Miscellaneous | - | 0 | 0 | - | 0 | 0 |
| Safety Factor | 10% / 10% | 274 | 18 | 10% | 6 | 0 |
| **>> Total Zone Loads** | **-** | **3012** | **198** | **-** | **69** | **0** |

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **TABLE 4.1.B. ENVELOPE LOADS FOR SPACE '' hvac control panel '' IN ZONE '' Zone 4 ''** | | | | | | |
|  |  |  |  | **COOLING** | **COOLING** | **HEATING** |
|  | **Area** | **U-Value** | **Shade** | **TRANS** | **SOLAR** | **TRANS** |
|  | **(m²)** | **(W/(m²-°K))** | **Coeff.** | **(W)** | **(W)** | **(W)** |
| **W EXPOSURE** |  |  |  |  |  |  |
| WALL | 10 | 0.642 | - | 107 | - | 26 |
| **H EXPOSURE** |  |  |  |  |  |  |
| ROOF | 12 | 0.510 | - | 128 | - | 24 |

**July DESIGN COOLING DAY, 1500**

**TABLE 1: SYSTEM DATA**

|  |  | **Dry-Bulb** | **Specific** |  |  | **Sensible** | **Latent** |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | **Temp** | **Humidity** | **Airflow** | **CO2 Level** | **Heat** | **Heat** |
| **Component** | **Location** | **(°C)** | **(kg/kg)** | **(L/s)** | **(ppm)** | **(W)** | **(W)** |
| Ventilation Air | Inlet | 41.0 | 0.03144 | 1586 | 400 | 32279 | 104082 |
| Vent - Return Mixing | Outlet | 28.8 | 0.01529 | 5750 | 526 | - | - |
| Central Cooling Coil | Outlet | 12.9 | 0.00895 | 5750 | 526 | 110034 | 107358 |
| Supply Fan | Outlet | 14.6 | 0.00895 | 5750 | 526 | 11510 | - |
| Cold Supply Duct | Outlet | 14.6 | 0.00895 | 5750 | 526 | - | - |
| Zone Air | - | 24.1 | 0.00914 | 5750 | 574 | 66036 | 3275 |
| Return Plenum | Outlet | 24.1 | 0.00914 | 5750 | 574 | 0 | - |

*Air Density x Heat Capacity x Conversion Factor: At sea level = 1.207; At site altitude = 1.206 W/(L/s-K)*

*Air Density x Heat of Vaporization x Conversion Factor: At sea level = 2947.6; At site altitude = 2944.1 W/(L/s)*

*Site Altitude = 10.0 m*

**TABLE 2: ZONE DATA**

|  | **Zone** |  |  |  |  |  | **Terminal** | **Zone** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | **Sensible** |  | **Zone** | **Zone** | **Zone** | **CO2** | **Heating** | **Heating** |
|  | **Load** | **T-stat** | **Cond** | **Temp** | **Airflow** | **Level** | **Coil** | **Unit** |
| **Zone Name** | **(W)** | **Mode** | **(W)** | **(°C)** | **(L/s)** | **(ppm)** | **(W)** | **(W)** |
| Zone 1 | 56153 | Cooling | 56041 | 24.5 | 4693 | 574 | 0 | 0 |
| Zone 2 | 3431 | Heating | 3966 | 20.0 | 640 | 534 | 208 | 0 |
| Zone 3 | 2947 | Deadband | 3033 | 25.7 | 225 | 635 | 0 | 0 |
| Zone 4 | 2976 | Cooling | 2995 | 27.5 | 192 | 623 | 0 | 0 |

**WINTER DESIGN HEATING**

**TABLE 1: SYSTEM DATA**

|  |  | **Dry-Bulb** | **Specific** |  |  | **Sensible** | **Latent** |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | **Temp** | **Humidity** | **Airflow** | **CO2 Level** | **Heat** | **Heat** |
| **Component** | **Location** | **(°C)** | **(kg/kg)** | **(L/s)** | **(ppm)** | **(W)** | **(W)** |
| Ventilation Air | Inlet | 6.0 | 0.00580 | 1586 | 400 | -29043 | 0 |
| Vent - Return Mixing | Outlet | 17.0 | 0.00580 | 5750 | 422 | - | - |
| Central Cooling Coil | Outlet | 17.0 | 0.00580 | 5750 | 422 | 0 | 0 |
| Supply Fan | Outlet | 18.7 | 0.00580 | 5750 | 422 | 11510 | - |
| Cold Supply Duct | Outlet | 18.7 | 0.00580 | 5750 | 422 | - | - |
| Zone Air | - | 21.2 | 0.00580 | 5750 | 430 | -12314 | 0 |
| Return Plenum | Outlet | 21.2 | 0.00580 | 5750 | 430 | 0 | - |

*Air Density x Heat Capacity x Conversion Factor: At sea level = 1.207; At site altitude = 1.206 W/(L/s-K)*

*Air Density x Heat of Vaporization x Conversion Factor: At sea level = 2947.6; At site altitude = 2944.1 W/(L/s)*

*Site Altitude = 10.0 m*

**TABLE 2: ZONE DATA**

|  | **Zone** |  |  |  |  |  | **Terminal** | **Zone** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | **Sensible** |  | **Zone** | **Zone** | **Zone** | **CO2** | **Heating** | **Heating** |
|  | **Load** | **T-stat** | **Cond** | **Temp** | **Airflow** | **Level** | **Coil** | **Unit** |
| **Zone Name** | **(W)** | **Mode** | **(W)** | **(°C)** | **(L/s)** | **(ppm)** | **(W)** | **(W)** |
| Zone 1 | -9904 | Heating | -9580 | 21.6 | 4693 | 430 | 26157 | 0 |
| Zone 2 | -1324 | Heating | -1303 | 19.7 | 640 | 430 | 2098 | 0 |
| Zone 3 | -1293 | Heating | -1261 | 19.6 | 225 | 430 | 1504 | 0 |
| Zone 4 | -69 | Deadband | -171 | 17.9 | 192 | 430 | 0 | 0 |



1. **Equipment Selection:**

**PACKAGE UNIT:**

**Equipment no :** **22-AHU-01-A,B**

Quantity : 2

with air cooled condensing unit (**22-ACCU-01A,B**)

**Cooling Coil :**

Cooling coil type : DX type

Cooling coil capacity : 217.4 kW

Cooling coil entering temperature : 28.8 °C db / 23°C wb

Cooling coil leaving air temperature : 12.9°C db / 12.6°C wb

**Blower:**

Supply Air Flow Rate: 5738 l/s  
Fresh Air Flow Rate: 1580 l/s  
Return Air Flow Rate: 4158 l/s

External Duct static pressure : 1.5 \* 95 m \* 0.816 pa/m =116.28 pa

Sound Attenuator Quantity: 2

Total Sound Attenuator Pressure Drop: 300 pa

Duct heater pressure drop: 58 pa

Motorized Fire Damper: 2\*29 pa = 58 pa

Motorized Damper: 2\*29 pa = 58 pa

Return Register: 48 pa

Supply Diffuser: 48 pa

Total External static pressure= 687 pa→700 pa

Internal static pressure : by vendor

**EXHAUST FANS:**

|  |  |  |  |
| --- | --- | --- | --- |
| Equipment No: | 22-EF-01-A,B | 22-EF-03 | 22-EF-04 |
| Quantity | 2 | 1 | 1 |
| Type | Centrifuge-roof mounted | Centrifuge-roof mounted | Centrifuge-roof mounted |
| Flow Rate(L/S) | 640 | 190 | 337 |
| Static Pressure | Duct:  7 m x 1.5 x 0.816 pa/m  =8.56 pa  Margin 10% = 0.85 pa  →9.5 pa  Exhaust Diffuser:  48 pa  Motorized Fire Damper:  29 pa  Motorized Damper:  29 pa  Exhaust Air Louver:  38 pa  =153.5 pa→160 pa | Duct:  12 m x 1.5 x 0.816  pa/m  =14.7 pa Margin 10% : 1.47  =16.17 pa  Exhaust Diffuser:  48 pa  Motorized Damper:  29 pa  Exhaust Air Louver:  38 pa  =131.2 pa→140 pa | Duct:  12 m x 1.5 x 0.816  pa/m  =14.7 pa Margin 10% : 1.47  =16.17 pa  Exhaust Diffuser:  48 pa  Volume Damper:  29 pa  Motorized Damper:  29 pa  Exhaust Air Louver:  38 pa  =160.17 pa→165 pa |
| Service Area | Battery Room | Prayer- pantry | Lavatory-shower &locker |
| Remarks |  |  |  |

**Duct Heater:**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 22-EDH-08 | 22-EDH-07 | 22-EDH-06 | 22-EDH-05 | 22-EDH-04 | 22-EDH-03 | 22-EDH-02 | 22-EDH-01 | Equipment No: |
| 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Quantity |
| 3.16 | 5.57 | 14.56 | 3.67 | 3.98 | 1.8 | 1.29 | 1.96 | Capacity: |
| 750\*200 | 525\*325 | 775\*450 | 375\*200 | 350\*275 | 350\*150 | 225\*175 | 300\*200 | Duct Size  (mm\*mm) |
| Battery Room | Engineering room  & Control Room | Auxiliary Room | Corridors& AAir lock | Offices & Archive &  Prayer | Pantry | Instrument Room | Lavatory & locker and shower | Service area |
|  |  |  |  |  |  |  |  | Remarks |