## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0767 |  |  | Transmital Date: 16/Jul/2022
Document Title: HVAC Calculation Note For Control Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-0767 |  |  | Transmital Date: 16/Jul/2022
[5 empty] | CRS No: NISOK-CRS-BK-GCS-PEDCO-120-HV-CN-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | دمای حباب تر غیرواقعی می‌باشد لذا لازم است دمای حباب تر و ارتفاع از سطح دریا و مقدار رطوبت مطابق نشریه 271 سازمان مدیریت و برنامه ریزی کشور و سازمان هواشناسی کشور اصلاح و محاسبات مجددا ارسال گردد. |  | 01/2294/27253 | 28/01/1401 | مبنای دمای محیط، مدرک Basic of Process Design پروژه است و دمای حباب تر محیط در این پروژه از عدد موجود در نشریه 271 بیشتر است و با توجه به رطوبت بالای بینک صلاح نیست که این عدد کمتر شود.
2 | لازم است قبل از پیوست فایل محاسبات بخش های Site Condition-Indoor Design Condition-Load Calculation Summary-Equipment Selection به مدرک اضافه گردد. |  | 01/2294/27253 | 28/01/1401 | انجام شد.
3 | نام مدرک در کلیه صفحات به اشتباه HVAC Design Criteria مقید شده است که می‌بایست اصلاح گردد. |  | 01/2294/27253 | 28/01/1401 | انجام شد.
4 | توضیحات بند دوم مدرک (Scop) مربوط به HVAC Design Criteria می باشد و می بایست مطابق با مدرک HVAC Calculation ارائه گردد. |  | 01/2294/27253 | 28/01/1401 | انجام شد.
5 | سایر بندهای مدرک مطابق با مدرک HVAC Calculation Note For Control Building مورد بازنگری قرار گیرند. |  | 01/2294/27253 | 28/01/1401 | با توجه به تغییرات اساسی در نقشه معماری ساختمان کنترل، مدرک HVAC Calculation Note For Control Building مورد بازنگری کلی قرار گرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 4/11/2022 |  |  |  |  | Date: 16/07/2022