## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0037 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0592 |  |  | Transmital Date: 2/13/2021
Document Title: Standard Drawing For Earth Pit |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-CV-TR-0592 |  |  | Transmital Date: 2/13/2021
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0037_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در یکی از برش های نقشه توضیح ذیل درج گردد. LIFTING BAR(HOOK BAR) |  | 1400-2294-413792 | 1400/11/30 | اعمال گردید .
| در NOTE به تیپ آرماتور اشاره گردد |  | 1400-2294-413792 | 1400/11/30 | در بند 3 نوت درج شده است.
| در NOTE قید گردد. All Excavation & Backfill for Concrete Work Shall Comply with Specification for Earth Work |  | 1400-2294-413792 | 1400/11/30 | اعمال گردید .
| در NOTE اشاره به LEAN CONCRETE شده است. چنانچه مورد نیاز نیست این شرح حذف گردد. |  | 1400-2294-413792 | 1400/11/30 | اعمال گردید .
2 | حداقل ابعاد مفید مطابق با استاندارد IPS-D-EL-401 مد نظر قرار گیرد. |  | 1400-2294-413792 | 1400/11/30 | مطابق با استاندارد گفته شده در نظر گرفته شده است
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: