## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-ME-SP-0002-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0015 |  |  | Transmital Date: 28/JUL/2021
Document Title: Specification For Atmospheric Above Ground Welded Steel Tanks |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-ME-TR-0015 |  |  | Transmital Date: 28/JUL/2021
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-ME-SP-0002-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | The followings shall be added to clause " 5.2.12" test and inspection: |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08
| 1-1-Tanks shall be hydrostatically tested in accordance with API STD 650 for a minimum period of 24 hours |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-2- hydro-test shall be don full of water |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-3-Roof manholes shall be open while filling or emptying a fixed roof tank for test purposes, so that excessive vacuum or pressure loading does not damage the tank |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-4-The Tank Vendor shall furnish all test materials and facilities, including blinds, bolting, and gaskets which is required for Hydrostatic test |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-5-Supply of treated and qualified water for hydro test shall be considered in tanks erector scope, unless otherwise specified in Purchase Order |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-6-Potable water shall be considered for Hydro test. Tank Erector is responsible for all requirements subjected for purchaser approval |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-7-Hydrostatic test of the tank include filling and emptying. The temperature of the test water shall be not lower than 20°C. |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-8-Hydrostatic test media shall be non-corrosive fresh water and free from sands |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-6-Tank erector shall measure settlement continuously during and after hydro test. The report shall be submitted for contractor review and decision |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-7-Uneven settlement of the tank on its foundation shall be reported immediately to the Inspector, and filling shall be stopped at any signs of excessive settlement pending a decision by the Inspector on the action to be taken |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
| 1-8-Any tank showing evidence of leakage from the bottom during water test should be emptied immediately. The source of such leaks should be determined and rectified. Where there is risk that the leakage may have caused washout of the foundation material, the foundations are to be nspected. The repair of the foundation should be subject to special consideration and approval by the Contractor |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | This paragraph has been added to the caluse 6.12 Due to addition of section 6 Material, heading for section 5.2.12 has been change to 6.12
2 | latest REV. of wind and siesmic publications /codes/ standards such as " siesmic design of oil facilities " code 038 / IBC CODE ,……..shall be added to refference list |  | BK-SUR-ENG-FXE-00-01277 | 2021-08-08 | American Society of Civil Engineers 7-10 (ASCE) is mentioned in the specification according to scope of work of the project.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: S.Salehi | Signature | M.Fakharian
| Date: 8/8/2021 |  |  |  |  | Date: 10/02/2021