## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LI-0001-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0957 |  |  | Transmital Date: 16-May-2022
Document Title: Electrical Load List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0957 |  |  | Transmital Date: 16-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-LI-0001-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | PEDCO Elec: Regarding to electrical equipment calculation such as AC&DC UPS calculation, Lighting calculation, etc. and process equipment list has not been submitted, so at this stage only structural comments has been mentioned and this document shall be submitted as IFA after submitting prerequisite documents (base on comment 2). |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | مدرک برق بر اساس مدرک Process Electrical Load List که با شماره ترنسمیتال 482 ارسال شده است، تولید شده است. لازم به ذکر است هر تغییر در مدرک فرآیند در مدرک برق نیز منعکس می شود. |  |  | Will be checked later.
2 | PEDCO Elec: This document shall be revised after finalizing or minor comments of following items : -Vendor data for packages -HVAC calculation for buildings. -Lighting and socket layout and these consumption -AC/DC UPS calculation. -Vendor data for pumps -Equipment List |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | هرگونه تغییر در مدارک مرتبط، در این مدرک لحاظ خواهد شد و این مدرک تغییر خواهد کرد. |  |  | Will be checked later.
3 | LV sheet: PEDCO Elec: According to basic load list and LV switchgear single line diagram some loads as below shall be added: -Welding socket A/B -Normal&Emergency lighting panel for control building -Cathodic protection (2 feeders instead of one Feeder) |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت. |  |  | Noted and Closed.
4 | MV sheet: PEDCO Elec: Transformer sizing description for fire water electric pump shall be added and specified. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | توان ترانس بر اساس مدرک Basic در نظر گرفته شده است. لازم به ذکر است سایز دقیق ترانس بعد از انجام مطالعات شبکه مشخص خواهد شد. |  |  | Noted and Closed.
5 | PEDCO Elec: Following items shall be modified for "AC&DC UPS": -Only one row shall be considered for each AC&DC UPS rated power. -Load Duty shall be considered continuous. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | با توجه به اینکه دیاگرام تک خطی براساس لیست بار تولید می شود، لذا تمام بارهای پروژه باید در این لیست ذکر گردد. همچنین یکی از ورودی های AC & DC UPS بر روی باس اضطراری و به صورت Continuous در نظر گرفته شده است. |  |  | Noted and Closed.
6 | MV sheet, Rows 5,6: PEDCO Elec: Calculated absorbed peak active and reactive power in LV sheet for transformers shall be considered in related cell in MV sheet. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Noted and Closed.
7 | MV sheet, Rows 5,6: PEDCO Elec: Related cell for following columns shall be filled: -Rated Power (Kw) -Eff. (%) -Power Factor and current normal operation(A) for power transformer should be calculated base on Rated Power(Kw). |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Noted and Closed.
8 | MV sheet: PEDCO Elec: "Demand load" title in load summary table of BUSA&B shall be modified to Peak Load and respectively the related description below tables A&B shall be modified. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 |  |  |  | Noted and Closed.
9 | PEDCO Elec: Value of Coolant factor shall be clarify in abbreviation sheet. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Noted and Closed.
10 | MV sheet: PEDCO Elec: Column "AA" title shall be modified from "Absorbed Peak Reactive Power (Kvar)" to "Absorbed Peak Aspirant Power (KVA)". |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Noted and Closed.
11 | LV sheet: PEDCO Elec: Tag of electrical equipment such as AC&DC UPS and DP/LP shall be modified base on our agreement. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | See below item 24.
12 | Calculation sheet, Section 6: PEDCO Elec: Motor/Feeder Type shall be specified for calculated method of electrical power demand (KW) . |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | تیپ فیدرها ی موتوری و غیر موتوری در ستون آخر اضافه گردید. |  |  | Noted and Closed.
13 | MV&LV Sheet: PEDCO Elec: A separated table shall be added and following items shall be specified: -Total peak load active power(KW) -Total peak load reactive power(KVAR) -Total peak load apparent power(KVA) |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال شد |  |  | Noted and Closed.
14 | LV Sheet: PEDCO Elec: one LV feeder for feeding each compressor auxiliary services such as oil pump, fan, internal lighting, etc. to be considered. Rating and service type to be finalized by Vendor |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Noted and Closed.
15 | LV Sheet: PEDCO Elec: It seems required LV auxiliary consumption for three fire water pump (2 diesel drive + one electric drive) such as battery charger for diesel types and motor heater for electric driven, have not been considered in load list, please clarify. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | See below item 25.
16 | PEDCO Mech&Process: Equipment and packages electrical load shall be updated and finalized base on vendor data. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | اعمال گشت |  |  | Will be checked later.
17 | PEDCO Mech: According to "Technical Specification for HVAC & Plumbing Design Basis" document, Each of MV/LV Switch Room, Control room and battery room shall be treated by 100% stand by split unit. In the case of a failure of the duty unit, stand by unit will automatically start. It shall be checked and modified (If required). |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | برای اتاق بانک خازنی تابلوی اضطراری اضافه گشت |  |  | See below item 28.
18 | PEDCO Process: According to mentioned rated power for air compressor in load list, even if it is assumed the current situation remains then rated power for air compressor will be more than 150KW . |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | تغییرات بر اساس لیست بار بخش فرآیند لحاظ گردید. |  |  | Noted and Closed.
19 | PEDCO Process: Air blower shall be added to load list. Even if it is assumed to has common feeder with ignition package, the rated power will be checked after providing ventilation capacity. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | تغییرات بر اساس لیست بار بخش فرآیند لحاظ گردید. |  |  | Noted and Closed.
20 | PEDCO Process: Rated power of air coolers will be checked after submitting mechanical data sheet. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | تغییرات بر اساس لیست بار بخش فرآیند لحاظ گردید. همچنین هر تغییر در هر زمان از پروژه در نظر گرفته خواهد شد. |  |  | Noted and Closed.
21 | PEDCO Process: It is necessary to modify the number of MOVs according to process diagram. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | بارهای MOV به روز رسانی گردید |  |  | Noted and Closed.
22 | PEDCO Process: According to lack of information provided by contractor for dehydration Package, It is not possible to check it. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | تغییرات بر اساس لیست بار بخش فرآیند لحاظ گردید. |  |  | Noted and Closed.
23 | PEDCO Process: BHP for Potable Water Pump (P-2209) shall be modified. |  | BK-SUR-ENG-ELE-00-02157 | 2021-11-30 | توانها بر اساس لیست بار بخش فرآیند لحاظ گردید. |  |  | Noted and Closed.
24 | Ref. item 11 above: Despite the consultant's response, DP/LP tag number shall be modified according to our agreement. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | نام تابلوها بر اساس گفتگوهای انجام شده تغییر پیدا کرد. |  |  | Noted and Closed.
25 | Ref. item 15 above: According to our telephone conversation, the feeders shall be considered base on the quantity of three fire water pump (2 diesel drive + one electric drive). (Has been considered for a diesel drive only) |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | دو عدد فیدر در نظر گرفته شد. |  |  | Noted and Closed.
26 | According to our telephone conversation following items shall be modified: |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16
26-1 | Rows 68, 69, 70: The description shall be modified to indicate that it is related to the compressors auxiliary service. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | عبارت Normal Panel for Gas Compressor اضافه گردید |  |  | Noted and Closed.
26-2 | Rows 75,62: The emergency lighting panel for capacitor room has been repeated in two rows. It shall be modified. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | ردیف 62 حذف گردید. |  |  | Noted and Closed.
27 | According to basic load list and single line diagram, cathodic protections will be fed from normal bus, not emergency bus. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | هر دو تابلوی حفاظت کاتدیک بر روی باس نرمال در نظر گرفته شده است. |  |  | Noted and Closed.
28 | PEDCO Mech: According to "Technical Specification for HVAC & Plumbing Design Basis" document, Each of MV/LV Switch Room, Control room and battery room shall be treated by 100% stand by split unit. In the case of a failure of the duty unit, stand by unit will automatically start. It shall be checked and modified (If required). |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بر لساس صحبتهای انجام با بخش HVAC این مشاور، فیدرهای این سیستم برای اتاق های LV، MV، بانک خازنی اضافه گردید. |  |  | Noted and Closed.
29 | :PEDCO Mech جهت ساختمان Electrical , Security, Switchgear Building مصارف HVAC مشخص نشده است يا به وضوح ذكر نشده است لطفا توضيح دهيد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | سیستم HVAC برای ساختمان سوییچگیر در نظر گرفته شد. لازم به ذکر است ساختمان Security در این پروژه وجود ندارد. |  |  | Noted and Closed.
30 | :PEDCO Process در بخش ولتاژ MV تخمين بار در مقطع فعلي قابل قبول بوده و لازم است پس از دريافت اطلاعات از سازندگان هر تجهيز اين مهم و تبعات آن در مدارك لحاظ گردد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بعد از نهایی شدن قرارداد خرید و مشخص شدن وندورها، مدرک لیست بار برق بر اساس آخرین اطلاعات هر وندور مورد بازنگری قرار خواهد گرفت. |  |  | Noted and Closed.
31 | PEDCO Process: در بخش ولتاژ LV مستنداتي در خصوص ميزان برق مورد نياز كولرهاي هوايي ارائه نشده است (نه محاسبات و نه وجود اعداد در داده برگ هاي بخش مكانيك) مطابق نقطه نظرات ارائه شده بر مدركي با همين عنوان در بخش فرايند توان كمپرسورهاي هوا نياز به بازنگري دارد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | این مدرک بر اساس مدرک Process Electrical Load List تهیه شده که به پیوست ارسال می گردد. از اینرو بازنگری در مدرک فرآیند منجر به تغییر در این مدرک خواهد شد که به تناسب آن تغییرات اعمال می گردد. |  |  | Will be checked later.
32 | :PEDCO Process در بخش ولتاژ LV ميزان بار پكيج نيتروژن پس از دريافت اطلاعات سازنده كمپرسور و اعمال آن در مدارك طراحي تفصيلي قابل بررسي مي باشد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بعد از نهایی شدن قرارداد خرید و مشخص شدن وندورها، مدرک لیست بار برق بر اساس آخرین اطلاعات هر وندور مورد بازنگری قرار خواهد گرفت. |  |  | Will be checked later.
33 | :PEDCO Process در بخش ولتاژ LV بار پكيج فلر ( بلوئر) ، پس از ارسال مدارك پيش نياز قابل بررسي مي باشد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بعد از نهایی شدن قرارداد خرید و مشخص شدن وندورها، مدرک لیست بار برق بر اساس آخرین اطلاعات هر وندور مورد بازنگری قرار خواهد گرفت. |  |  | See below item 38
34 | :PEDCO Process در بخش ولتاژ LV ميزان بار پكيج نمزدا پس از دريافت اطلاعات سازنده و اعمال آن در مدارك طراحي تفصيلي قابل بررسي مي باشد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بعد از نهایی شدن قرارداد خرید و مشخص شدن وندورها، مدرک لیست بار برق بر اساس آخرین اطلاعات هر وندور مورد بازنگری قرار خواهد گرفت. |  |  | Will be checked later.
35 | :PEDCO Process در بخش ولتاژ LV رديف 19 در صورتي كه صرفا مرتبط با بلوئر پكيج فلر مي باشد نيازي به در نظر گرفتن در بار اضطراري نمي باشد. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | بر اساس تغییرات در مدرک فرآیندی، این بار بر روی باس اضطراری قرار گرفت. |  |  | Noted and Closed.
36 | :PEDCO Process در بخش ولتاژ LV ضروريست جداول مدرك در ويرايش بعدي قابليت خوانا بودن در حالت كاغذي (Hard Copy) را دارا باشند. |  | BK-SUR-ENG-ELE-00-03082 | 2022-02-16 | اعمال گردید. |  |  | Noted and Closed.
37 | According to our telephone conversation "HVAC feeder" shall be modified "Split feeder" for rows 76 to 81 on load description column. |  | BK-SUR-ENG-ELE-01-03789 | 2022-04-09 | اعمال گردید. |  |  | Noted and Closed.
38 | See above item 33: پاسخ داده شده در خصوص ارائه بار بلوئر پس از انتخاب سازنده قابل قبول نبوده و لازم است تخمين اوليه توسط پيمانكار صورت پذيرد. |  | BK-SUR-ENG-ELE-01-03789 | 2022-04-09 | بر اساس مدرک تولیدی بخش فرآیند که با ترنسمیتال 723، ارسال شده است، توان مورد نیاز بار بلوئر در این مدرک در نظر گرفته شده است. لازم به ذکر است در صورت تغییر بار، این مدرک به روزرسانی خواهد شد. |  |  | Will be checked later.
39 | This document shall be revised base on above mentioned comments (items 1,2,31,32, 34 and 38, if required). |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29
40 | Lighting panels power shall be rechecked and modified after finalizing or minor comments on lighting calculation and SLD for buildings, area and shelter. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29
41 | It shall be clarify why type of Jocky pumps outgoing feeders has not been considered motor type. Meanwhile Jocky pumps will be fed from emergency bus so the related bus on "bus" column shall be modified. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | با توجه به اینکه موتورهای آب آتش نشانی شامل موتورهای جوکی و موتور اصلی در اسکوپ کار وندور است، لذا نحوه روشن و خاموش شدن آن و کنترل آن توسط وندور و اداوت ابزاردقیق صورت میگیرد. از اینرو بخش برق فقط کابل مورد نیاز و تأمین برق آن را به عهده دارد و در این صورت این فیدر به صورت یک فیدر غیرموتوری خواهد بود.
42 | service type for split coolers feeders need to modification. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | تیپ فیدرهای Split تغییر پیدا کرد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: