## Air
Instrument & Plant Air Consumption
Item | Qty. |  | Unit Cons. | Total Cons. | Unit | Inlet Nozzle Sizing
On/Off Valve | 41 | 100% | 0.64 | 26.24 | Nm3/hr |  | Variable |  | Unite
Control Valve | 29 | 100% | 0.64 | 18.56 | Nm3/hr | A constant used during inlet nozzle sizing | ɛ | 6000
Dehydration | 1 | 100% | 20 | 20 | Nm3/hr | A constant used during gas outlet nozzle sizing | X | 3750
Variable Pitch air cooler | 6 | 100% | 1 | 6 | Nm3/hr | Gas Density | ρv | 9.3 | Kg/m3
Gas Compressor Instrument Air | 3 | 100% | 7 | 21 | Nm3/hr | Gas Flowrate | Qv | 19.8649 | m3/hr
Total Instrument Air Consumption | - |  |  | 91.8 | Nm3/hr | Liquid Density | ρL | 9.3 | Kg/m3
30% Over Design |  |  |  | 119.34 | Nm3/hr | Liquid Flowrate | QL | 0.01
Total Instrument Air Consumption |  |  |  | 119.34 | Nm3/hr | ( Inlet mixture density ) | ρin | 9.3 | Kg/m3
Air Dryer Regenration |  |  | 20% | 23.868 | Nm3/hr |  | Vin | 25.4 | m/s
Dryer Inlet |  |  |  | 143.208 | Nm3/hr | The product (ρin*Vin^2 )shall not exceed ɛ | ρin Vin^2 | TRUE
Plant Air |  |  |  | 30 | Nm3/hr |  | Ain | 0.00021735 | m2
Air Compressor Outlet |  |  |  | 173.208 | Nm3/hr | Calculated inlet nozzle diameter | Din | 0.65495 | in
115.4 |  | 44.8 |  | 190.5288 |  |  | Selected Nozzle | 2 | in
Air Receiver Capacity | [5 empty] | Note : ε should be 1000 when no inlet device is foreseen. ε should be 1500 when a half-open pipe is used. ε should be 6000 when a vane pack is used
Item | Value | Unit
Barometric Pressure P0 | 1.03
Initial Air Receiver Pressure P1 | 8 | barg
Final Air Receiver Pressure P2 | 4.5 | barg |  |  |  | Gas Outlet Nozzle Sizing
Air Receiver Retention time | 15 | min |  |  |  |  | Variable |  | Unite
Total Plant Air Consumption | 119.34 | Nm3/hr |  |  |  | A constant used during inlet nozzle sizing | ɛ | 6000
Total Plant Air Consumption | 125.8935 | Sm3/hr |  |  |  | A constant used during gas outlet nozzle sizing | X | 3750
Max. Air Receiver Required Vol. | 9.2622 | m3 |  |  |  | Gas Density | ρv | 9.3 | Kg/m3
[6 empty] | Gas Flowrate | Qv | 19.8649 | m3/hr
Air Receiver Sizing (Vertical) | [5 empty] | Liquid Density | ρL | 9.3 | Kg/m3
Item | Value | Unit | Value | Unit |  | Liquid Flowrate | QL | 0.01
Height (H) | 5000 | mm | 5 | m |  | ( Inlet mixture density ) | ρin | 9.3 | Kg/m3
Diameter (ID) | 1500 | mm | 1.5 | m |  |  | VgOut | 20.0805 | m/s
Radius | 750 | mm | 0.75 | m |  | The product (ρin Vin^2 )shall not exceed ɛ | ρin*Vin^2 | TRUE
Type of Head | Elliptical | [5 empty] | AgOut | 0.0002748 | m2
Depth of Head | 375 | mm | 0.375 | m |  | Calculated inlet nozzle diameter | DgOut | 0.73642 | in
Liquid Level | 300 | mm | 0.3 | m | 8.8313 |  | Selected Nozzle | 2 | in
Nominal Capacity | 9.7193 |  | m3 | 9.2622
Note on F5: Roshanak Haditalab: Based on IPS-E-PR-330.
Note on F6: Roshanak Haditalab: Based on IPS-E-PR-330.
Note on M17: Ghazale Ataie: Minimum nozzle size=2 in
Note on M35: Ghazale Ataie: Minimum nozzle size=2 in

## Nitrogen
Nitrogen Consumption
Item | Qty. | Unit Cons. | Total Cons. | Unit
Gas Compressor | 3 | 6 | 18 | Nm3/hr
Methanol Injection Pack. | 1 | 1 | 1 | Nm3/hr
Lean Glycol Tank Blanketing | 1 | 17 | 17 | Nm3/hr
Glycol Sump Vessel | 1 | 3.5 | 3.5 | Nm3/hr | 20.5
Total Nitrogen |  |  | 39.5 | Nm3/hr
10% Over Design + Total |  |  | 43.45 | Nm3/hr
Plant Air |  | 3.7 | 146.15 | Nm3/hr
160.765
Nitrogen Receiver Vessel Sizing
Item | Value | Unit
Barometric Pressure P0 | 1.03
Initial Air Receiver Pressure P1 | 8 | barg
Final Air Receiver Pressure P2 | 4 | barg
Air Receiver Retention time | 15 | min
Total Plant Nitrogen Consumption | 43.45 | Nm3/hr
Total Plant Nitrogen Consumption | 45.8361 | Sm3/hr
Max. Nitrogen Receiver Required Vol. | 2.9507 | m3
Nitrogen Receiver Sizing (Vertical)
Item | Value | Unit | Value | Unit
Height (H) | 3150 | mm | 3.15 | m
Diameter (ID) | 1050 | mm | 1.05 | m
Radius | 525 | mm | 0.525 | m
Type of Head | Elliptical
Depth of Head | 262.5 | mm | 0.2625 | m
Liquid Level | 300 | mm | 0.3 | m
Nominal Capacity | 3.0307 |  | m3 | 2.9507
Note on E11: Roshanak Haditalab: 3 ~ 4

## Potable Water
Tank Sizing (Vertical)
Item | Value | Unit
Height (H) | 2.6 | m
Diameter (ID) | 3.5 | m
HLL | 2.25 | m
LLL | 0.15 | m
Nominal Capacity | 25.0023 | m3
Working Capacity | 20.1941 | m3 | 17.5
Elevation | 6 | m
Water Consumption
Person | 10
Usage | 125 | lit/day.person
Usage | 0.125 | m3/day.person
Total Consumption | 1.25 | m3/day
Hold-Up | 14 | day
Total Vol. | 17.5 | m3
Usage | 0.052083 | m3/hr

## Diesel Oil (2)
Corrosion Consumption
Injec. Point | Qty. | Q max. | Q max. total | Diesel max. | Diesel min. | Q total max. | Q total min. | Unit
Gas From Binak | 1 | 4.991 | 4.991 | #REF! | #REF! | #REF! | #REF! | lit/hr
Gas From Golkhari | 1 | 9.582 | 9.582 | #REF! | #REF! | #REF! | #REF! | lit/hr
V-2105 Outlet | 1 | 14.57 | 14.57 | #REF! | #REF! | #REF! | #REF! | lit/hr
V-2103 Outlet | 1 | 14.51 | 14.51 | #REF! | #REF! | #REF! | #REF! | lit/hr
V-2205 Outlet | 1 | 0.006507 | 0.006507 | #REF! | #REF! | #REF! | #REF! | lit/hr
Pipeline | 1 | 14.45 | 14.45 | #REF! | #REF! | #REF! | #REF! | lit/hr
Total |  |  | 58.1095 | #REF! | #REF! | #REF! | #REF! | lit/hr
Total | [5 empty] | #REF! | #REF! | m3/hr | #REF!
[9 empty] | #REF! | 14 DAY | 60 BAR PUMP
Diesel Generator Consumption
Generato Size | 500 | kW
Diesel Consumption | 35.7 | gal/hr
Diesel Consumption | 0.13495 | m3/hr |  | 1.8904
Diesel Consumption | 3.2387 | m3/day
Fire Diesel Pump Consumption
Qty. | 2
Rated Capacity | 398 | m3/hr
Diff. Pressure | 8.2 | bar
Density | 850 | kg/m3
Hydraulic Power | 90.6556 | kW
Total Hydraulic Pow. | 181.3111 | kW
Efficiency | 60%
BHP | 302.1852
Diesel Consumption | 62.9552 | lit/hr
Diesel Consumption | 0.074065 | m3/hr
Diesel Consumption | 1.7776 | m3/day
Fuel Oil Storage Drum Calculation(Diesel generator)
Drum Diameter | 1.5 | m
Drum Length | 3 | m
Drum Total Volume | 5.9641 | m3
Maximum Fuel Oil Consumption | #REF! | m3/hr
HLL | 1.25 | m
LLL | 0.15 | m
Liquid Volume HLL | 5.3343 | m3
Liquid Volume LLL | 0.29446 | m3
Storage Volume (between HLL & LLL) | 5.0398 | m3
Fuel Oil Storage Drum Calculation(fire Diesel pump)
Drum Diameter | 1.2 | m
Drum Length | 3 | m
Drum Total Volume | 3.6644 | m3
Maximum Fuel Oil Consumption | #REF! | m3/hr
HLL | 0.95 | m
LLL | 0.15 | m
Liquid Volume HLL | 3.1218 | m3
Liquid Volume LLL | 0.25645 | m3
Storage Volume (between HLL & LLL) | 2.8654 | m3
Note on G5: Roshanak Haditalab: Based on 70/30 in yellow row.
Note on D16: Roshanak Haditalab: Based on vendor data.
Note on D29: Roshanak Haditalab: 5 lit/day per kW

## Closed Drain drum
Vessel Sizing (Horizontal) |  |  |  |  | Vessel Sizing (Horizontal) Slug Catcher
Item | Value | Unit | Value | Unit | Item | Value | Unit | Value | Unit
Length (L) | 7800 | mm | 7.8 | m | Length (L) | 12600 | mm | 12.6 | m
Diameter (ID) | 2600 | mm | 2.6 | m | Diameter (ID) | 4200 | mm | 4.2 | m
Radius | 1300 | mm | 1.3 | m | Radius | 2100 | mm | 2.1 | m
Type of Head | Elliptical |  |  |  | Type of Head | Elliptical
Depth of Head | 650 | mm | 0.65 | m | Depth of Head | 1050 | mm | 1.05 | m
HHLL | 2300 | mm | 2.3 | m | HHLL | 3900 | mm | 3.9 | m
HLL | 2150 | mm | 2.15 | m | HLL | 3750 | mm | 3.75 | m
LLL | 300 | mm | 0.3 | m | LLL | 250 | mm | 0.25 | m
LLLL | 150 | mm | 0.15 | m | LLLL | 150 | mm | 0.15 | m
Nominal Capacity | 46.0139 |  | m3 |  | Nominal Capacity | 193.9619 |  | m3
Vol. from Bottom to HLL | 40.8574 |  | m3 |  | Vol. from Bottom to HLL | 183.2891 |  | m3
Vol. from Bottom to LLL | 2.8277 |  | m3 |  | Vol. from Bottom to LLL | 4.424 |  | m3
Working Capacity | 38.0297 |  | m3 |  | Working Capacity | 178.8651 |  | m3 | 37.3
Elevation | - |  | m |  | Elevation | - |  | m
Based on Slug Catcher drum bottom to LLL . & Inlet K.O. Drum bottom to HLL.
Vessel Sizing (Horizontal) Inlet K.O. drum
[5 empty] | Item | Value | Unit | Value | Unit
[5 empty] | Length (L) | 4500 | mm | 4.5 | m
[5 empty] | Diameter (ID) | 1500 | mm | 1.5 | m
[5 empty] | Radius | 750 | mm | 0.75 | m
[5 empty] | Type of Head | Elliptical
[5 empty] | Depth of Head | 375 | mm | 0.375 | m
[5 empty] | HHLL | 1200 | mm | 1.2 | m
[5 empty] | HLL | 1050 | mm | 1.05 | m
[5 empty] | LLL | 800 | mm | 0.8 | m
[5 empty] | LLLL | 150 | mm | 0.15 | m
[5 empty] | Nominal Capacity | 8.8357 |  | m3
[5 empty] | Vol. from Bottom to HLL | 6.6384 |  | m3
[5 empty] | Vol. from Bottom to LLL | 4.7992 |  | m3
[5 empty] | Working Capacity | 1.8392 |  | m3 | 37.3
[5 empty] | Elevation | - |  | m
Note on O17: Roshanak Haditalab: Based on slug catcher drum capacity from bottom to NLL. ID: 3600 mm, L:10800 mm, NLL: 1500 mm
Note on O36: Roshanak Haditalab: Based on slug catcher drum capacity from bottom to NLL. ID: 3600 mm, L:10800 mm, NLL: 1500 mm

## Glycol Sump Drum
Vessel Sizing (Horizontal)
Item | Value | Unit | Value | Unit
Length (L) | 3600 | mm | 3.6 | m
Diameter (ID) | 1100 | mm | 1.1 | m
Radius | 550 | mm | 0.55 | m
Type of Head | Elliptical
Depth of Head | 275 | mm | 0.275 | m
HHLL | 800 | mm | 0.8 | m
HLL | 650 | mm | 0.65 | m
LLL | 300 | mm | 0.3 | m
LLLL | 150 | mm | 0.15 | m
Nominal Capacity | 3.7696 |  | m3
Vol. from Bottom to HLL | 2.3256 |  | m3
Vol. from Bottom to LLL | 0.81945 |  | m3
Working Capacity | 1.5062 |  | m3 | 1.5
Elevation | - |  | m
Note on G17: Roshanak Haditalab: Besed on vendor data.

## Oily Sump
Rain Rate
Item | Value | Unit
Length 1 | 170 | m
Width 1 | 27 | m
Length 2 | 18 | m
Width 2 | 10.5 | m
Length 3 | 8 | m
Width 3 | 6 | m
Length 4 |  | m
Width 4 |  | m
Area | 4827 | m2
Max. Rainfall | 101.51 | mm/hr
Max. Rainfall | 0.10151 | m/hr
Max. Rainfall | 0.0016918 | m/min
Max. Rainfall | 0.00084592 | m/min
Sump Sizing
Item | Value | Unit
Hold-Up time | 15 | min
Rainfall | 0.012689 | m
Rain Volume | 61.2486 | m3
Length (L) | 3 | m
Hight (H) | 3 | m
Width (W) | 4 | m
HLL | 2.7 | m
Full Volume | 36 | m3
Usable Volume | 32.4 | m3 | 61.2486
Note on D5: Roshanak Haditalab: Based on piping plot plan.
Note on D6: Roshanak Haditalab: Based on piping plot plan.
Note on D7: Roshanak Haditalab: Based on piping plot plan.
Note on D8: Roshanak Haditalab: Based on piping plot plan.
Note on D14: Roshanak Haditalab: Based on client's data.

## Methanol
Tank Sizing (Vertical)
Item | Value | Unit
Rated Flow Rate | 15.73 | lit/hr
Total Flow Rate | 0.01573 | m3/hr
Storage Time | 7 | day
Storage Volume | 2.6426 | m3
Diameter | 1.2 | m |  | 12.5
Height | 2.6 | m
HLL |  | m
LLL |  | m
Nominal Capacity | 2.939 | m3
Working Capacity |  | m3 | 2.6426

## Corrosion
Tank Sizing (Vertical)
Item | Value | Unit
Low Pre. Flow Rate | #REF! | lit/hr
High Pre. Flow Rate | #REF! | lit/hr
Total Flow Rate | #REF! | lit/hr
Total Flow Rate | #REF! | m3/hr
Storage Time | 7 | day |  | 1310
Storage Volume | #REF! | m3
Diameter | 1 | m
Height | 1.5 | m
HLL |  | m
LLL |  | m
Nominal Capacity | 1.1775 | m3
Working Capacity |  | m3 | #REF!

## fuel gas
purge gas pressure
| barg | ft/s | m/s | in | m | A(m2) | Am3/s | Am3/hr | kg/hr
Flare header size | 0.5 | 0.1 | 0.03048 | 16 | 0.4064 | 0.12972 | 0.0039538 | 14.2336 | 21
ignition panel cosumption | [8 empty] | 5
Dehydration | [8 empty] | 30
Blanketing | [7 empty] | 10 | 14

## Sheet2
FIRE WATER |  |  | DISEIL GENERATOR
Fuel Oil Storage Drum Calculation |  |  | Fuel Oil Storage Drum Calculation
Drum Diameter | 1.2 | m | Drum Diameter | 1.5 | m
Drum Length | 3 | m | Drum Length | 3 | m
Drum Total Volume | 3.6644 | m3 | Drum Total Volume | 5.9641 | m3
Maximum Fuel Oil Consumption | 2.7 | m3/hr | Maximum Fuel Oil Consumption | 5 | m3/hr
HLL | 0.95 | m | HLL | 1.25 | m
LLL | 0.15 | m | LLL | 0.15 | m
Liquid Volume HLL | 3.1218 | m3 | Liquid Volume HLL | 5.3343 | m3
Liquid Volume LLL | 0.25645 | m3 | Liquid Volume LLL | 0.29446 | m3
Storage Volume (between HLL & LLL) | 2.8654 | m3 | Storage Volume (between HLL & LLL) | 5.0398 | m3
SLUGE CATCHER
Fuel Oil Storage Drum Calculation
|  |  | Drum Diameter | 4.2 | m
|  |  | Drum Length | 12.5 | m
|  |  | Drum Total Volume | 213.9123 | m3
|  |  | Maximum Fuel Oil Consumption | 5 | m3/hr
|  |  | HLL | 3.375 | m
|  |  | LLL | 0.25 | m
|  |  | Liquid Volume HLL | 185.7856 | m3
|  |  | Liquid Volume LLL | 4.6083 | m3
|  |  | Storage Volume (between HLL & LLL) | 181.1774 | m3