## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | EL | DT | 0010 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | Jul.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | SEP.2021 |  | IFC |  |  |  | M.Asgharnejad |  |  | M.Fakharian |  | Sh.Ghalikar
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-707395
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | EL | DT | 0010 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | [6 empty] | 54
5 | X | [7 empty] | 55
6 | X | X | X | [5 empty] | 56
7 | X | X | [6 empty] | 57
8 | X | [7 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## 11-0.42
Transformer Identification Number: TR-12, TR-15, TR-5, TR-007, TR-046
Item | Description | Purchaser Requirement | Manufacturer Data
1-GENERAL
1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
1.2 | Manufacturer's Name | By Vendor
1.3 | Quantity | Well12-TR-01, Well15-TR-01, Well05-TR-01, Well07-TR-01, Well46-TR-01
1.4 | Transformer Operation Mode (Single or in Parallel) | Single |  | D02
1.5 | Standard | IPS-M-EL-152 (3), BK-GNRAL-PEDCO-000-EL-SP-0004
1.6 | Kind/Construction of Transformer | Oil Immersed, Separate High & Low Windings, Two Winding
1.7 | Transformer Type (Sealed/Conservator) | Oil Immersed, Hermitically Sealed With Pillow Nitrogen
1.8 | Rated Power in Service Condition | 250 KVA
1.9 | Nominal Frequency & Frequency Variation | 50 Hz ± 5 %
1.10 | Winding Connection/Vector Group | Dyn11
1.11 | Nominal Primary Voltage, Phase to Phase & Voltage Variation | 11000 V ± 10 %
1.12 | Nominal Secondary Voltage (no load), Phase to Phase & Phase to Neutral | 420 V / 242 V
1.13 | Tap Changer | ±5% in 2.5% Steps, off Load, on HV Winding
1.14 | Cooling System | ONAN
1.15 | Insulating Lliquid | Mineral Oil
2-Environmental Conditions (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001)
2.1 | Installation | Outdoor, Safe Area, Under Shelter
2.2 | Hazardous Area Classification | Safe Area
2.3 | Altitude (Above Sea Level) | 12.5 m
2.4 | Ambient Temperature | Min ~ Max: +5 ~ +52°C
2.5 | Relative Humidity | 100%
2.6 | Climate | Corrosive, Hot Atmosphere
3-Primary Winding Voltage Ratings
3.1 | Highest System Voltage | 12 KV
3.2 | Rated Lightning Impulse Withstand Voltage | 75 KV
3.3 | Rated Short Duration Power Frequency Withstand Voltage (rms) | 28 KV
3.4 | Load Rejection Overvoltage (for Generator Transformer) | Not Applicable
4-Secondary Winding Voltage Ratings
4.1 | Highest System Voltage | 1 KV
4.2 | Rated Lightning Impulse Withstand Voltage | 8 KV
4.3 | Rated Short Duration Power Frequency Withstand Voltage (rms) | 3 KV
4.4 | Neutral Earthing System (Solidly Earthed / Resistance Earthed) | Solidly Earthed
4.5 | Insulation Type | By Vendor
4.6 | Insulation Class | Class A
4.7 | Average Winding Temperature Rise (55°C Ambient) | Acc. to IEC 60076-2, Clause 4.2
4.8 | Top Oil Temperature Rise (55°C Ambient) | Acc. to IEC 60076-2, Clause 4.2
4.9 | Oil Preservation System | Not Applicable (Sealed Type)
4.10 | Short Circuit Level of MV System | Primary: 25 kA for 1 seconds
4.11 | Required Short Circuit Impedance (if Different From Standard Values) | No
4.12 | Required Short Circuit Impedance @75°C | 4%
4.13 | Zero Sequence Impedance | By Vendor
4.14 | X/R Ratio at Principal Tap | By Vendor
4.15 | Efficiency at Full Load & PF=0.8 Lag (100% Load) | By Vendor
4.16 | Efficiency at Full Load & PF=0.8 Lag (75% Load) | By Vendor
4.17 | Efficiency at Full Load & PF=0.8 Lag (50% Load) | By Vendor
5-Primary Winding Characteristics
5-.1 | Reactance [Ω] | By Vendor
5.2 | Resistance[Ω] @ 75°C | By Vendor
6-Secondary Winding Characteristics
6.1 | Reactance[Ω] | By Vendor
6.2 | Resistance[Ω] @ 75°C | By Vendor
Equipment Tag Number: TR-12, TR-15, TR-5, TR-007, TR-046
Item | Description | Purchaser Requirement | Manufacturer Data
7-Tolerances
7.1 | Voltage Ratio at Principal Tap & No-load | ±0.5 %
7.2 | Voltage Ratio at Other Tapping | ±0.5 %
7.3 | Short Circuit Impedance at Principal Tap | ±10% of declared value
7.4 | Short Circuit Impedance at Other Tapping | ±15% of declared value
7.5 | Anticipated Unbalance Loading in Percent of Rated Power | 10%
7.6 | Core Construction | Laminated Silicon Steel
7.7 | Flux Density in the Magnetic Circuit @Nominal Frequency & Voltage | By Vendor
7.8 | No-Load Losses at Rated Voltage & Principal Tap [W] | By Vendor
7.9 | I2R Loss at Rated Current & Principal Tap | By Vendor
7.1 | Stray Load Loss at Rated Current & Principal Tap | By Vendor
7.11 | Full Load Total Loss [W] | By Vendor
7.12 | Inrush Current | By Vendor
7.13 | Short Circuit Loss | By Vendor
7.14 | Primary Cable Type & Size | Based on BK-SSGRL-PEDCO-110-EL-LI-0002
7.15 | External Terminations, Primary Side (Exposed Bushings/Cable Box) | Cable Box
7.16 | Secondary Cable Type & Size | Based on BK-SSGRL-PEDCO-110-EL-LI-0002
7.17 | External Terminations, Secondary Side (Exposed Bushings/Cable Boxes ) | Cable Box
7.18 | Type & Size of Cable Glands (Power Cable) | By Vendor
7.19 | Type & Size of Cable Glands (Control Cable) | By Vendor
7.20 | Dimension (W x D x H) [mm] | By Vendor
7.21 | Total Weight [kg] | By Vendor
7.22 | Weight of Transformer Without Oil | By Vendor
7.23 | Noise Level Limit (at 1m from Transformer) [dB] | Less than 85 dB(A) Based on IEC 60076-10
7.24 | Oil Volume [liter] | By Vendor
7.25 | Oil Weight [kg] | By Vendor
7.26 | Oil Characteristics (Name/ Type/ Flash Point) | Acc. to IEC 60296
8-Auxiliary Equipment
8.1 | Top Oil Temperature Indicator With Alarm & Trip Contacts | Required
8.2 | Pressure Relief Device with Contact (Shall Be Operated by Internal Pressure of Nitrogen) | Required
8.3 | Sudden Pressure Relief Valve With Contact | Required
8.4 | Oil Level Indicator with Contacts (Low & High) Magnetic Type | Required (Magnetic Type)
8.5 | Gas Pressure & Vacuum Indicator for Internal Pressure of Nitrogen Gas | Required
8.6 | Oil Drain/ Sampling Device | Required
8.7 | Earth Terminal | Required (2 Point on the Bottoms of the Tank)
8.8 | LV Terminal Box with Gland Plate | Required
8.9 | HV Terminal Box with Gland Plate | Required
8.10 | Instrument Connection Terminal Box | Required (Min IP55)
8.11 | Arching Horn | Not Required
8.12 | Drain Valve | Required
8.13 | Wheels, Bidirectional (Turn Able by 90°) | Required
8.14 | Lugs | Fixed to the Tanks for Lifting the Complete Transformer
8.15 | Lifting & Pulling Yes | Required
8.16 | CT to Be Supplied by (Transformer Manufacturer/Purchaser) | Transformer Manufacturer
8.17 | Neutral CT Ratio, Class & Burden | 300/1A, 5P20, 10VA
8.18 | Rating Plate | Stainless Steel
8.19 | Accessory Equipment Contacts Current / Voltage Rating | 5A / 250VAC
8.20 | Transformer Radiator | Welded
8.21 | Transformer Cover | To be Welded to the Tank With a Continuous Weld
8.22 | Thickness of Radiator Plate | By Vendor
8.23 | Thickness of Tank Wall, Base & Cover | By Vendor
8.24 | Tank Painting Specification | By Vendor
8.25 | Radiator Painting Specification | By Vendor
Equipment Tag Number: TR-12, TR-15, TR-5, TR-007, TR-046
Item | Description | Purchaser Requirement | Manufacturer Data
8-Auxiliary Equipment
8.26 | Tank & Radiator Color | By Vendor
8.27 | Accessory Equipment Contacts Type | Dry Type
8.28 | Routine Tests Including | IEC60076
| a) Measurement of Winding Resistance | Witness & Report
| b) Measurement of Voltage Ratio & Check of Voltage Vector Relationship | Witness & Report
| c) Measurement of Impedance Voltage (Principal tapping) Short-Circuit Impedance & Load Loss | Witness & Report
| d) Measurement of no-Load Loss & Current | Witness & Report
| e) Impedance & Load Losses at Rated Current on Principal Tap | Witness & Report
| f) Applied Potential & Induced Potential Tests | Witness & Report
| g) Dielectric Tests | Witness & Report (IEC60076-3)
8.29 | Type Test | Test Report on the Same Design Transformer is Required
8.30 | Painting & Finish | Manufacture Standard
8.31 | Special Tools if Any | By Vendor
8.32 | Deviation from this Specification if Any | By Vendor
9-Notes
* | All required accessories shall be considered by vendor.
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 3 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 4 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 5 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK

## 33-0.42
Transformer Identification Number: TR-14
Item | Description | Purchaser Requirement | Manufacturer Data
1-GENERAL
1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
1.2 | Manufacturer's Name | By Vendor
1.3 | Quantity | Well14-TR-01
1.4 | Transformer Operation Mode (Single or in Parallel) | Single |  | D02
1.5 | Standard | IPS-M-EL-152 (3), BK-GNRAL-PEDCO-000-EL-SP-0004
1.6 | Kind/Construction of Transformer | Oil Immersed, Separate High & Low Windings, Two Winding
1.7 | Transformer Type (Sealed/Conservator) | Oil Immersed, Hermitically Sealed With Pillow Nitrogen
1.8 | Rated Power in Service Condition | 250 KVA
1.9 | Nominal Frequency & Frequency Variation | 50 Hz ± 5 %
1.10 | Winding Connection/Vector Group | Dyn11
1.11 | Nominal Primary Voltage, Phase to Phase & Voltage Variation | 33000 V ± 10 %
1.12 | Nominal Secondary Voltage (no load), Phase to Phase & Phase to Neutral | 420 V / 242 V
1.13 | Tap Changer | ±5% in 2.5% Steps, off Load, on HV Winding
1.14 | Cooling System | ONAN
1.15 | Insulating Lliquid | Mineral Oil
2-Environmental Conditions (Process Basis Design, BK-GNRAL-PEDCO-000-PR-DB-0001)
2.1 | Installation | Outdoor, Safe Area, Under Shelter
2.2 | Hazardous Area Classification | Safe Area
2.3 | Altitude (Above Sea Level) | 12.5 m
2.4 | Ambient Temperature | Min ~ Max: +5 ~ +52°C
2.5 | Relative Humidity | 100%
2.6 | Climate | Corrosive, Hot Atmosphere
3-Primary Winding Voltage Ratings
3.1 | Highest System Voltage | 36 KV
3.2 | Rated Lightning Impulse Withstand Voltage | 170 KV
3.3 | Rated Short Duration Power Frequency Withstand Voltage (rms) | 70 KV
3.4 | Load Rejection Overvoltage (for Generator Transformer) | Not Applicable
4-Secondary Winding Voltage Ratings
4.1 | Highest System Voltage | 1 KV
4.2 | Rated Lightning Impulse Withstand Voltage | 8 KV
4.3 | Rated Short Duration Power Frequency Withstand Voltage (rms) | 3 KV
4.4 | Neutral Earthing System (Solidly Earthed / Resistance Earthed) | Solidly Earthed
4.5 | Insulation Type | By Vendor
4.6 | Insulation Class | Class A
4.7 | Average Winding Temperature Rise (55°C Ambient) | Acc. to IEC 60076-2, Clause 4.2
4.8 | Top Oil Temperature Rise (55°C Ambient) | Acc. to IEC 60076-2, Clause 4.2
4.9 | Oil Preservation System | Not Applicable (Sealed Type)
4.10 | Short Circuit Level of MV System | Primary: 25 kA for 1 seconds
4.11 | Required Short Circuit Impedance (if Different From Standard Values) | No
4.12 | Required Short Circuit Impedance @75°C | 4%
4.13 | Zero Sequence Impedance | By Vendor
4.14 | X/R Ratio at Principal Tap | By Vendor
4.15 | Efficiency at Full Load & PF=0.8 Lag (100% Load) | By Vendor
4.16 | Efficiency at Full Load & PF=0.8 Lag (75% Load) | By Vendor
4.17 | Efficiency at Full Load & PF=0.8 Lag (50% Load) | By Vendor
5-Primary Winding Characteristics
5-.1 | Reactance [Ω] | By Vendor
5.2 | Resistance[Ω] @ 75°C | By Vendor
6-Secondary Winding Characteristics
6.1 | Reactance[Ω] | By Vendor
6.2 | Resistance[Ω] @ 75°C | By Vendor
Transformer Identification Number: TR-14
Item | Description | Purchaser Requirement | Manufacturer Data
7-Tolerances
7.1 | Voltage Ratio at Principal Tap & No-load | ±0.5 %
7.2 | Voltage Ratio at Other Tapping | ±0.5 %
7.3 | Short Circuit Impedance at Principal Tap | ±10% of declared value
7.4 | Short Circuit Impedance at Other Tapping | ±15% of declared value
7.5 | Anticipated Unbalance Loading in Percent of Rated Power | 10%
7.6 | Core Construction | Laminated Silicon Steel
7.7 | Flux Density in the Magnetic Circuit @Nominal Frequency & Voltage | By Vendor
7.8 | No-Load Losses at Rated Voltage & Principal Tap [W] | By Vendor
7.9 | I2R Loss at Rated Current & Principal Tap | By Vendor
7.1 | Stray Load Loss at Rated Current & Principal Tap | By Vendor
7.11 | Full Load Total Loss [W] | By Vendor
7.12 | Inrush Current | By Vendor
7.13 | Short Circuit Loss | By Vendor
7.14 | Primary Cable Type & Size | Based on BK-SSGRL-PEDCO-110-EL-LI-0002
7.15 | External Terminations, Primary Side (Exposed Bushings/Cable Box) | Cable Box
7.16 | Secondary Cable Type & Size | Based on BK-SSGRL-PEDCO-110-EL-LI-0002
7.17 | External Terminations, Secondary Side (Exposed Bushings/Cable Boxes ) | Cable Box
7.18 | Type & Size of Cable Glands (Power Cable) | By Vendor
7.19 | Type & Size of Cable Glands (Control Cable) | By Vendor
7.20 | Dimension (W x D x H) [mm] | By Vendor
7.21 | Total Weight [kg] | By Vendor
7.22 | Weight of Transformer Without Oil | By Vendor
7.23 | Noise Level Limit (at 1m from Transformer) [dB] | Less than 85 dB(A) Based on IEC 60076-10
7.24 | Oil Volume [liter] | By Vendor
7.25 | Oil Weight [kg] | By Vendor
7.26 | Oil Characteristics (Name/ Type/ Flash Point) | Acc. to IEC 60296
8-Auxiliary Equipment
8.1 | Top Oil Temperature Indicator With Alarm & Trip Contacts | Required
8.2 | Pressure Relief Device with Contact (Shall Be Operated by Internal Pressure of Nitrogen) | Required
8.3 | Sudden Pressure Relief Valve With Contact | Required
8.4 | Oil Level Indicator with Contacts (Low & High) Magnetic Type | Required (Magnetic Type)
8.5 | Gas Pressure & Vacuum Indicator for Internal Pressure of Nitrogen Gas | Required
8.6 | Oil Drain/ Sampling Device | Required
8.7 | Earth Terminal | Required (2 Point on the Bottoms of the Tank)
8.8 | LV Terminal Box with Gland Plate | Required
8.9 | HV Terminal Box with Gland Plate | Required
8.10 | Instrument Connection Terminal Box | Required (Min IP55)
8.11 | Arching Horn | Not Required
8.12 | Drain Valve | Required
8.13 | Wheels, Bidirectional (Turn Able by 90°) | Required
8.14 | Lugs | Fixed to the Tanks for Lifting the Complete Transformer
8.15 | Lifting & Pulling Yes | Required
8.16 | CT to Be Supplied by (Transformer Manufacturer/Purchaser) | Transformer Manufacturer
8.17 | Neutral CT Ratio, Class & Burden | 300/1A, 5P20, 10VA
8.18 | Rating Plate | Stainless Steel
8.19 | Accessory Equipment Contacts Current / Voltage Rating | 5A / 250VAC
8.20 | Transformer Radiator | Welded
8.21 | Transformer Cover | To be Welded to the Tank With a Continuous Weld
8.22 | Thickness of Radiator Plate | By Vendor
8.23 | Thickness of Tank Wall, Base & Cover | By Vendor
8.24 | Tank Painting Specification | By Vendor
8.25 | Radiator Painting Specification | By Vendor
Transformer Identification Number: TR-14
Item | Description | Purchaser Requirement | Manufacturer Data
8-Auxiliary Equipment
8.26 | Tank & Radiator Color | By Vendor
8.27 | Accessory Equipment Contacts Type | Dry Type
8.28 | Routine Tests Including | IEC60076
| a) Measurement of Winding Resistance | Witness & Report
| b) Measurement of Voltage Ratio & Check of Voltage Vector Relationship | Witness & Report
| c) Measurement of Impedance Voltage (Principal tapping) Short-Circuit Impedance & Load Loss | Witness & Report
| d) Measurement of no-Load Loss & Current | Witness & Report
| e) Impedance & Load Losses at Rated Current on Principal Tap | Witness & Report
| f) Applied Potential & Induced Potential Tests | Witness & Report
| g) Dielectric Tests | Witness & Report (IEC60076-3)
8.29 | Type Test | Test Report on the Same Design Transformer is Required
8.30 | Painting & Finish | Manufacture Standard
8.31 | Special Tools if Any | By Vendor
8.32 | Deviation from this Specification if Any | By Vendor
9-Notes
* | All required accessories shall be considered by vendor.
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 6 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 7 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK
تسهیلات
DATA SHEETS FOR POWER TRANSFORMERS OF WELL PADS
شماره صفحه: 8 از 8
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0010
D02
بسته کاری
SSGRL
پروژه
BK