## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DT-0006_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0651 |  |  | Transmital Date: 27-Feb-2022
Document Title: Data Sheets for LV Capacitor Bank of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0651 |  |  | Transmital Date: 27-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-DT-0006_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Following items shall be modified and finalizing base on load list, cable list, network study, single line diagram for capacitor bank and capacitor bank sizing: -Bus bar rated current -Size and Type of cables -Rating of capacitor bank -Short circuit level -Metering &Protection device |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-20 | بعد از تولید مدرک لیست بار و انجام محاسبات بانک خازنی این مدرک مورد بازنگی قرار گرفت. لازم به ذکر است هر گونه تغییر در بارهای الکتریکی که منجر ه تغییر در محاسبات گردد، در این مدرک لحاظ خواهد شد. |  |  | Will be checked later.
2 | This data sheet shall be in accordance with attached IPS-M-EL-186(2) data sheet. For example following items shall be added -Type and size of cable glands (power) cable /s ) -Type and size of cable glands(control cable /s) -Enclosure ventilation (natural or forced air cooling ) ,... . |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | مطابق با فایل ارسالی کارفرمای محترم، این مدرک مورد بازنگری قرار گرفت. همچنینی استاندارد 181 بانک خازنی اضافه گردید. |  |  | See below item 4.
3 | A 40kVAR capacitor bank breaker size will be about 100A, but in raw 3.6 it mentioned 2000A. It seems consultant have not enough focus on project requirements. At the other hand this size of capacitor bank can be fixed type or an small automatic regulaing wall mounted panel type. data sheet to be modified as per project requirements. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | مطابق با فایل ارسالی کارفرمای محترم، این مدرک مورد بازنگری قرار گرفت. همچنینی استاندارد 181 بانک خازنی اضافه گردید. |  |  | See below item 5.
4 | Ref. item 2 above: Type and size of control cable/s shall be specified.(For example sample voltage and current and interlock with diesel generator.) |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | در ردیف 5 از بند 4 اضافه گردید.
5 | Ref. item 3 above: (Page 3, Item 3.6/Page 5, Item 9.3) It seems the rated current of bus bar and CB has not been selected correctly as below calculation: 50KVAR/(1.732*0.4)=72, 72*1.5=109A |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | مطابق با ویرایش جدید مدرک محاسبات بانک خازنی مدرک فوق اصلاح گردید.
6 | Page 3, Item 3.7/Page 5, Item 9.4: Rated short circuit level shall be rechecked and modified. Short circuit level shall be modified after finalizing or minor comments on Electrical Network (Load Flow, Motor Starting & Short Circuit) Study Report of Well Pads |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | مطابق با مطالعات شبکه برق و ترنسمیتال 1082 سطح اتصال کوتاه بارهای LV در ایستگاه تقویت فشار گاز 24 کیلو آمپر می باشد. لذا با وجود افت سطح اتصال کوتاه به واسطه طول مسیر ایستگاه تا تسهیلات سر چاهی، جهت حاشیه امنیت سطح اتصال کوتاه تابلو به جای 25 عدد 31.5 کیلو آمپر در نظر گرفته شده است.
7 | Page 4, Item 5.2: Rating of each Capacitor Bank shall be modified base on comments on Calculation Note For LV Capacitor Bank of Well Pads. |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | اعمال گردید.
8 | Page 5, Item 9.2: The MCCB shall be selected Fixed type instead of withdrawable type. More over CB shall be seleted 4 Pole instead of 3 pole. |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | اعمال گردید.
9 | Page 5, Item 9.7: Voltage protection shall be added. |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | اعمال گردید.
10 | Rated insulation voltage shall be added and specified. |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | اعمال گردید.
11 | IRPs will be equipped with VFD. Using power factor correction capacitors generally is not required for VFD controlled motors due to capacitors transient voltage can tripped the VFD or damage it. at the other hand power factor in the VFD line side in near to unity. In case of using a VFD in a capacitor compensated system there are some technical considerations for capacitors selections. anyway at this stage this document shall not be revised before IRP Manufacturer data and recommendations received. above mentioned comments shall be considered just in case of using capacitor bank recommended by IRP Manufacturer. |  | BK-SUR-ENG-ELE-00-03377 | 2022-03-07 | نوت 3 با موضوع در نظر گرفتن نیاز مندی های بین بانک خازنی و VFD توسط وندور اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 07-Mar-22 |  |  |  |  | Date: