## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0662 |  |  | Transmital Date: 02-Mar-2022
Document Title: Overall Single Line Diagram of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0662 |  |  | Transmital Date: 02-Mar-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-SL-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | According to agreement in endorsement stage, DS/ES shall be deleted at the beginning of the transmition lines of well No. BK12,BK.15, BK.05, BKW046SB, W007SBD. And only the Cut out fuse plus LBS+Earth switch considered instead of DS/ES. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | مطابق درخواست کارفرمای محترم اصلی پروژه و توضیحات تفصیلی در پاسخ به نظرات ایشان و همچنین نقشه های بیسیک پروژه، در محل های انشعاب برای تغذیه چاه ها (انشعاب در محل برج شماره 9 خط تراکم گاز به نمک زدایی و انشعاب در گنتری ابتدایی پست تراکم گاز) از LBS و سكسيونر؛ و در پست های بیرونی سر چاه ها از LBS و كات اوت فيوز استفاده و در نقشه ها نمایش و درج شده است.
2 | It shall be clarify why two CT has been considered on neutral of transformers. It shall be modified base on comments on single line diagram. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | در نوترال ترانس و مطابق نقشه های بیسیک پروژه؛ یک CT با دو کور جهت حفاظت های مربوطه ترانس منظور شده است که همانگونه که مستحضرید حتی در صورت عدم استفاده از یکی از کورها تاثیر فنی/ قیمتی روی ترانس نخواهد داشت.
3 | Note 2 on page 2 shall be modified. (According to scope of work and supply only 1 circuit transmission line is contractor scope of suuply.) Meanwhile Notes1 &2 shall be mentioned on diagram. (Like as note 3) |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | اصلاحات لازم در نت ها انجام گردید.
4 | No. of pages 9 and 10 on page 2 shall be modified to pages 5 and 6. |  | BK-SUR-ENG-ELE-00-03469 | 2022-03-12 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 12-Mar-22 |  |  |  |  | Date: