## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0005-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0541 |  |  | Transmital Date: 02-Feb-2022
Document Title: Single Line Diagram For Capacitor Banks of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0541 |  |  | Transmital Date: 02-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-SL-0005-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | IRPs will be equipped with VFD. Using power factor correction capacitors generally is not required for VFD controlled motors due to capacitors transient voltage can tripped the VFD or damage it. at the other hand power factor in the VFD line side in near to unity. In case of using a VFD in a capacitor compensated system there are some technical considerations for capacitors selections. anyway at this stage this document shall not be revised before IRP Manufacturer data and recommendations received. following comments shall be considered just in case of using capacitor bank recommended by IRP Manufacturer. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | نوت 8 با موضوع در نظر گرفتن نیاز مندی های بین بانک خازنی و VFD توسط وندور اضافه گردید.
2 | This document shall be revised base on comments on "Calculation Note For LV Capacitor Bank Of Well Pads" document. (steps size of capacitor bank, incoming and bus bar rated current) |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | مطابق با آخرین ویرایش مدرک محاسبات اصلاح گردید.
3 | Incoming feeder current rating and number of poles shall be compatible with outgoing feeder for capacitor bank in LV switchgear. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | کلید ورودی به صورت 4 پل و با ظرفیت 125 آمپر در نظر گرفته شده است.
4 | Short circuit level shall be modified after submitting network study. (If required) |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | مطابق با مطالعات شبکه برق که با ترنسمیتال 1082 سطح اتصال کوتاه بار های LV در ایستگاه تقویت فشار گاز 24 کیلو آمپر می باشد. لذا با وجود افت سطح اتصال کوتاه به واسطه طول مسیر ایستگاه تا تسهیلات سر چاهی، جهت حاشیه امنیت سطح اتصال کوتاه تابلو به جای 25 عدد 31.5 کیلو آمپر در نظر گرفته شده است.
5 | Voltage sample for APFR shall be shown in single line diagram. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | با توجه به اینکه Automatic Power Factor Regulator تجهیز تنظیم کننده بانک خازن است، در لجند مدرک اضافه گردید.
6 | Normal/Fault signal lamp shall be considered for outgoing feeders. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | چراغ سیگنال روشن/خاموش و خطا برای خروجی ها اضافه گردید.
7 | Voltage protection (27/47/59) shall be added for incoming feeder. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | یک عدد PHC برای در نظر گرفتن رله های ولتاژی اضافه گردید.
8 | Signal lamp for phases shall be added for incoming feeder. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | چراغ سیگنال های هر فاز در کلید ورودی نشان داده شده است.
9 | It should be clarified about how to supply the control voltage in the capacitor bank panel. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | نوت شماره 9 هم در مدرک دیاگرام تک خطی و هم در مدرک داده برگ بانک خازنی با موضوع در نظر گرفتن یک عدد ترانس ایزوله خشک توسط سازنده تابلو جهت استفاده در مدار کنترلی اضافه گردید.
10 | It seems the signal lamp for incoming CB shall be modified base on type of MCCB CB. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | چراغ سیگنال های مورد نیاز تابلو اضافه گردیده است.
11 | APFR abbreviation shall be added on legend page. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | در لجند مدرک اضافه گردیده است.
12 | The symbols in SLD shall be selected base on legend pages, for example incoming CB is MCCB, but the symbol in SLD is not corrected. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | مطابق با سیمبل پروژه اصلاح گردید.
13 | Following note shall be added: All capacitors shall be provided with a discharge resistor, characteristics of which shall be specified by vendor. Capacitors must discharge to a residual voltage less than 75v within 3 minutes. |  | BK-SUR-ENG-ELE-00-03060 | 2022-02-14 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 13-Feb-2022 |  |  |  |  | Date: