## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-HV-DC-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0624 |  |  | Transmital Date: 22/Feb/2022
Document Title: HVAC & Plumbing Design Criteria |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-HV-TR-0624 |  |  | Transmital Date: 22/Feb/2022
[5 empty] | CRS No: NISOK-CRS-BK-GCS-PEDCO-120-HV-CN-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | clause 1: (GENERAL DEFINITION) |  | 00/2294/443215 | 1400/12/19 | COMPANY term HAS REPLACED WITH CLIENT.
2 | CLOUSE 7.2: EXTERNAL DESIGN CONDITIONS |  | 00/2294/443215 | 1400/12/19 | Has up to deted according to "PROCESS BASIS OF DESIGN" document D04 .
3 | CLOUSE 8: INTERNAL DESIGN CONDITIONS |  | 00/2294/443215 | 1400/12/19 | Has up to deted according to new architected drawings and related internal design conditions.
4 | 9.3 DUST |  | 00/2294/443215 | 1400/12/19 | filters efficiency has correct.
5 | 15.1.1.CONTROL BUILDING |  | 00/2294/443215 | 1400/12/19 | EXHAUST FAN FOR BATTERY ROOM HAS CONSIDERD.(duty / stand by)
6 | 15.1.2. SWITCHGEAR BUILDING OF WELL PADS |  | 00/2294/443215 | 1400/12/19 | EXHAUST FAN FOR BATTERY ROOM HAS CONSIDERD.
7 | 17.1.2. RE-CIRCULATED AIR FILTRATION REQUIREMENTS |  | 00/2294/443215 | 1400/12/19 | for final filter bag filter is enough.
8 | 18.1.2. EXTENSION OF EXISTING ELEC. BUILDING |  | 00/2294/443215 | 1400/12/19 | Has up to deted according to new architected drawings and spaces which has requierd new HVAC system.
9 | 18.1.3. SWITCHGEAR BUILDING OF WELL PADS |  | 00/2294/443215 | 1400/12/19 | Has up to deted according to new architected drawings.
10 | 13.1 HEAT GAINS FROM LIGHTING |  | 00/2294/443215 | 1400/12/19 | 25w/m2 has replaced with 20w/m2 according to received advices from electric and instrument discipline.
11 | 13.3 HEAT GAINS FROM EQUIPMENT |  | 00/2294/443215 | 1400/12/19 | electrical heat gain quantities for some spaces has changed according to received new data from electric and instrument discipline. Well pad substation has added to table.
12 | 20.1 DUCTING REQUIREMENTS |  | 00/2294/443215 | 1400/12/19 | "Duct work is Low Pressure class." has added.
12 | 20.1 DUCTING REQUIREMENTS |  | 00/2294/443215 | 1400/12/19 | rectangular ducts dimensions(thickness of sheet for construction of ducts with dimentions up to 30cm has changed to 0.6mm)
13 | 21.3 PLUMBING WATER SYSTEM |  | 00/2294/443215 | 1400/12/19 | pantry sink hot water demand has added.
| 15.0 STANDBY EQUIPMENT AND DESIGN MARGINS |  | 00/2294/443215 | 1400/12/19 | VFD building has removed.
15 | 15.1.2. SWITCHGEAR BUILDING OF WELL PADS |  | 00/2294/443215 | 1400/12/19 | "Battery room exhaust fan" has added according to contract.
16 | 18.1.4. SECURITY BUILDING OF WELL PADS |  | 00/2294/443215 | 1400/12/19 | emergency power has considerd for hvac system.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 4/11/2022 |  |  |  |  | Date: 20/07/2022