## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DG-0001_D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0780 |  |  | Transmital Date: 06 APR 2022
Document Title: Block Diagram Configuration For Control/ESD/F&G System - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-IN-T-0780 |  |  | Transmital Date: 06 APR 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-DG-0001_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق مدارک پایه ارتباط سریال FACP با سیستم DCS نمایش داده شود. |  | 01/2294/54898 | 1401/02/19 | از آنجا که دربسته Manifold تنها سیستم FACP برای دتکتورهای داخل ساختمان کنترل طراحی شده است و فضای فرایندی به لحاظ F&G پایش نمیشود،نیاز به ارتبط این سیستم با سیستم DCS نمیباشد . لازم به ذکر است این سیستم امکان ایجاد دستور ESD برای محوطه فرآیندی را نیزدارا نمی باشد در نتیجه نیازی به ارتباط سریال FACP با سیستم DCS نمی باشد.
2 | مانیتورها32 اینچ صنعتی در نظر گرفته شوند. |  | 01/2294/54898 | 1401/02/19 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
3 | در قالب Note اعلام گردد که شبکه پرینترها از شبکه مانیتورینگ مستقل خواهد بود. |  | 01/2294/54898 | 1401/02/19 | در قالب Note در مدرک اعلام گردید که شبکه پرینترهای Engineering workstation از شبکه مانیتورینگ مستقل هستند اما پرینترOperator workstation داخل شبکه مانیتورینگ می باشند.
4 | تجهیزات Fire Alarm متناسب برای تمام ساختمان های برق (سوییچ روم، اتاق باطری شارژر/UPSو اتاق باتری و...) نمایش داده شود. |  | 01/2294/54898 | 1401/02/19 | مدرک اصلاح گردید. تجهیزات Fire Alarm مطابق مدرکPLOT PLAN" "DRAWING-EXTENSION OF BINAK B/C MANIFOLD تنها در ساختمان کنترل در نظر گرفته می شوند و از Switchgear room نیزحذف گردیدند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 29 Jan 2022 |  |  |  |  | Date: