## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | IN | DT | 0003 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | JUL.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707370
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | IN | DT | 0003 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0003 |  | D02
REFERENCE DOCUMENTS:
1- SPECIFICATION FOR INSTRUMENTATION | [8 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
2-PIPELINE MATERIAL SPECIFICATION | [8 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
3- PIPING & INSTRUMENT DIAGRAM:
| P&ID - W018S | [7 empty] | BK-W018S-PEDCO-110-PR-PI-0001
| P&ID - W028 | [7 empty] | BK-W028-PEDCO-110-PR-PI-0001
| P&ID - W035 | [7 empty] | BK-W035-PEDCO-110-PR-PI-0001
| P&ID - W008N | [7 empty] | BK-W008N-PEDCO-110-PR-PI-0001
| P&ID - W007S | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| P&ID - W046S | [7 empty] | BK-W046S-PEDCO-110-PR-PI-0001
4-PROCESS FLOW DIAGRAM (PFD) | [8 empty] | BK-GCS-PEDCO-120-PR-PF-0001
5-INSTRUMENT & CONTROL SYSTEM DESIGN CRITERIA | [8 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
6- SPECIFICATION FOR WHCP/HPU | [8 empty] | BK-SSGRL-PEDCO-110-IN-SP-0001

## Note
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0003 | D02
GENERAL NOTES:
1 - Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
2- Material Test Certificate and calibration Certificate for all gauges to be submitted by Vendor.
3- All field instruments shall be furnished with a stainless steel corrosion resistant nameplate permanently fastened with screws and stamped as follows and as applicable:
· Vendor’s name
· Model number
· Serial number
· Instrument tag number
· Operating range
· hazardous area certification & certification agency name
· Pressure rating
4- Environmental Condition For Field Instrumentation Of BINAK Oil field Shall Be Considered As Per The Following:
• Minimum ambient temperature (°C): -5 °C • Maximum ambient temperature (°C): 50 °C • Maximum steel surface exposed to sun (°C): 85 °C • Maximum Design relative humidity: 100% • Minimum Design relative humidity: 0%

## TG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK |  | SSGRL |  | PEDCO |  | 000 |  | IN |  | DT | 0003 |  | D02
DATA SHEETS FOR TEMPERATURE GAUGE
GENERAL | 1 | Item No. | [13 empty] | See List
| 2 | Tag Number | [13 empty] | See List
| 3 | Service | [13 empty] | See List
| 4 | Fluid | [8 empty] | State |  |  |  |  | See List
| 5 | Line Number /Equipment | [13 empty] | See List
| 6 | Line Size | [8 empty] | Line Rating |  |  |  |  | See List
| 7 | P&ID No. | [13 empty] | See List
| 8 | Nozzel Length (mm) | [13 empty] | See List
| 9 | Nace Requirement | [13 empty] | See List (Note 10)
PROCESS CONDITIONS | 10 | Velocity (m/s) | [8 empty] | Density (Kg/m3) |  | Density (Kg/m3) |  |  | See List |  |  | See List
| 11 | Temp. ᵒC |  |  |  |  | Oper. | [5 empty] | Design |  |  | See List |  |  |  | See List
| 12 | Press. Barg |  |  |  |  | Oper. | [5 empty] | Design |  |  | See List |  |  |  | See List
CONNECTION & CASE | 13 | Case Type | [13 empty] | hermetically sealed
| 14 | Ingress Protection | [13 empty] | IP65
| 15 | Case Diameter | [13 empty] | 150 mm (6'')
| 16 | Connection Size To Thermowell | [13 empty] | 1/2" NPTM
| 17 | Ring Style | [13 empty] | V.T.A
| 18 | Stem Length | [8 empty] | Stem Diameter |  |  |  |  | Suit for Well (VTA) |  |  | 6 mm
| 19 | Stem Material | [8 empty] | Stem Location |  |  |  |  | S.S 316 |  |  | Every angle
| 20 | Case/Ring Material | [13 empty] | S.S 304
| 21 | Window Material | [13 empty] | shatterproof glass
| 22 | Connector Material | [13 empty] | S.S 316 Zero AdjustmentDial Color
| 23 | Exterior Treat. Color | [13 empty] | polished SS
DIAL & POINTER | 24 | Element Type | [8 empty] | Dial Scale Type |  |  |  |  | bi-metallic (Note 5) |  |  | DUAL
| 25 | Zero Adjustment |  |  |  |  | Matrail Pointer | [5 empty] | Dial Color |  |  | adjustable pointer. external calibration |  |  | AISI 304 or aluminum |  | WHITE WITH BLACK FIGURES
| 26 | Dial Material |  |  |  |  | Accuracy | [5 empty] | Dial Size |  |  | aluminium |  | Better than ± 1% of full span |  | 150 mm
| 27 | Range Min. | Range Min. | Range Min. | Range Min. | Range Min. | Range Min. |  | Range Min. | Range Min. | Max. |  | Max. |  | Max. | See List |  |  | See List
THERMOWELL | 28 | ConstructionType | ConstructionType | ConstructionType | ConstructionType | ConstructionType | ConstructionType |  | ConstructionType | ConstructionType | Shank Style |  | Shank Style |  | Shank Style | drilled bar stock |  |  | Tapered
| 29 | Process Conn. | Process Conn. | Process Conn. | Process Conn. | Process Conn. | Process Conn. |  | Process Conn. | Process Conn. | Instrument Conn. |  | Instrument Conn. |  | Instrument Conn. | See List |  |  | 1/2" NPTF
| 30 | Bore Diameter | Bore Diameter | Bore Diameter | Bore Diameter | Bore Diameter | Bore Diameter |  | Bore Diameter | Bore Diameter | Outside Dia. @ Top |  | Outside Dia. @ Top |  | Outside Dia. @ Top | V.T.A |  |  | V.T.A
| 31 | Outside Dia. @ Tip | Outside Dia. @ Tip | Outside Dia. @ Tip | Outside Dia. @ Tip | Outside Dia. @ Tip | Outside Dia. @ Tip |  | Outside Dia. @ Tip | Outside Dia. @ Tip | Insertion Length "U" (See Note 13) |  | Insertion Length "U" |  | Insertion Length "U" | V.T.A |  |  | See List
| 32 | Lag Ext. Len. "T" | Lag Ext. Len. "T" | Lag Ext. Len. "T" | Lag Ext. Len. "T" | Lag Ext. Len. "T" | Lag Ext. Len. "T" |  | Lag Ext. Len. "T" | Lag Ext. Len. "T" | Thermowell Mat. / Flange Mat. |  | Thermowell Mat. |  | Thermowell Mat. | V.T.A |  |  | S.S 316L
SPECIAL | 33 | Custom Tag | [13 empty] | SS permanent attached
| 34 | Compliance Code | [13 empty] | -
PURCHASE | 35 | Manufacturer | [13 empty] | Will be finalized later
| 36 | Model | [13 empty] | Will be finalized later
Notes: 1- V.T.A: Vendor to Advise, N/A: Not Applicable, VTC:Vendor to Confirm 2- Thermowell is included for all Temperature Indicators. 3- Temperature gauges shall be fully adjustable type (Every Angle). 4- Temperature gauges shall be double scale type (°C and °F). 5- All gauges shall be bi-metallic type 6- Window shall be heavy plate glass, breakage resistance and shatter proof. 7- Type of mounting shall be direct bottom entry. 8- Well length shall be suitable for stem length. 9- On insulated lines, thermowells shall include a 64 mm lagging extension as per ips-c-in-120. 10- NACE requirement to be as per MR-0175/ISO 15156 if mentioned in data sheet. 11- Thermowell wake frequency analysis (stress calculation) according to ASME Power Test Code 19.3 shall be done & submitted by vendor. 12- Temperature elements shall be capable of withstanding intermittent over-ranging to 1.5 times the maximum scale. 13- Standard Number for U-Length is IPS-D-IN-101.
D02

## LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR TEMPERATURE GAUGE - WELLHEADS
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال | نسخه |  | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK |  | SSGRL |  | PEDCO |  | 000 | IN |  | DT |  | 0003 | D02
Item | Tag No. | Service | P&ID |  | Equipment/ Line No. |  | Fluid |  | State | Line Size | Velocity (m/s) | Measuring Range (bar) |  | Pressure Oper. (barg)SUM/WIN | Pressure Des. (barg) | Oper. Tem. (°C)SUM/WIN | Design Tem. (°C) | Density (Kg/m3) (Gas/ Oil/ Water) | NACE | Proccess. Conn. | Conn. Rating | Nozzel Length. (mm) | U Length (mm) | Remark | Revision
1 | TG/TW-1201 | W007S | BK-W007S-PEDCO-110-PR-PI-0002 |  | CRD-110-121-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 0.776 | 0-160 |  | 16.38/16.50 | 205.8 | 79.98/79.92 | 105 | 349.44 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
2 | TG/TW-1601 | W008N | BK-W008N-PEDCO-110-PR-PI-0001 |  | CRD-110-161-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 0.528 | 0-160 |  | 11.89/12.11 | 205.8 | 74.02/73.32 | 105 | 344.64 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
3 | TG/TW-1101 | W018S | BK-W018S-PEDCO-110-PR-PI-0001 |  | CRD-110-111-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 0.424 | 0-160 |  | 15.60/16.57 | 205.8 | 73.98/73.44 | 105 | 429.43 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
4 | TG/TW-1401 | W028 | BK-W028-PEDCO-110-PR-PI-0001 |  | CRD-110-141-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 1.628 | 0-160 |  | 20.44/20.39 | 205.8 | 79.93/79.67 | 105 | 416.35 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
5 | TG/TW-1501 | W035 | BK-W035-PEDCO-110-PR-PI-0001 |  | CRD-110-151-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 1.516 | 0-160 |  | 22.48/22.46 | 205.8 | 79.85/79.64 | 105 | 447.3 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
6 | TG/TW-1301 | W046S | BK-W046S-PEDCO-110-PR-PI-0001 |  | CRD-110-131-LN15-6"-PT |  | HC WATER + |  | LIQUID/ GAS | 6" | 0.957 | 0-160 |  | 20.88/21.07 | 205.8 | 79.15/78.50 | 105 | 424.78 | Yes | Flanged 1 1/2 RTJ | API 3000 | 200 | 250
D02