## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DG-0001_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0828 |  |  | Transmital Date: 17 Apr 2022
Document Title: Instrument Earthing Typical Diagram |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0828 |  |  | Transmital Date: 17 Apr 2022
[5 empty] | CRS No: CRS-PEDCO-BK-GCS-PEDCO-120-IN-DG-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مورد 1 نظر خاصی مطرح نمی باشد. |  | 01/2294/59512 | 1401/02/22 | -
2 | در خصوص مورد 2، این مدرک تنها مدارک ارتینگ ابزاردقیق می باشد و بعنوان مدرک اصلی در نظر گرفته می شود و بنابراین عبارت TYPICAL از مدارک حذف گردد و متناسب نوع سیستم کنترلی و کابلهای استفاده شده در هر واحد سیستم ارتینگ مربوطه برای تابلو ها ( نام تابلو) و کابلها (تگ کابلها) مشخص گردد. |  | 01/2294/59512 | 1401/02/22 | مطابق MDL تایید شده و توافقات صورت گرفته و همچنین مطابق روال معمول سایر پروژه ها مدرک EARTH ابزاردقیق به صورت TYPICAL ارسال می گردد. DETAIL کابل کشی مطابق با LAYOUT بخش الکتریکال انجام شده و در مدرک MTO بخش الکتریکال خرید می گردد که Note مربوط به آن به مدرک اضافه گردید. این مدرک صرفا جهت نمایش فلسفه EARTHING بخش ابزاردقیق برای استفاده سایر دیسیپلین ها تولید می گردد.
3 | در خصوص مورد 3، مجزا بودن چاهک های ارت PE، IS، NIS و همچنین فاصله بین چاهک های PEو CE حداقل 20 متر بصورت NOTE در مدارک ذکر گردد. |  | 01/2294/59512 | 1401/02/22 | نظرات کارفرمای محترم در مدرک اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 7 May 2022 |  |  |  |  | Date: