## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR 11 KV OVER HEAD LINE EQUIPMENT
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 52
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | EL | DT | 0012 | D04
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR 11 KV OVER HEAD LINE EQUIPMENT نگهداشت و افزایش تولید میدان نفتی بینک
D04 |  | Jul.2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D03 |  | Feb.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | Jan.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Dec.2021 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Nov.2021 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-707397
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR 11 KV OVER HEAD LINE EQUIPMENT
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 52
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | EL | DT | 0012 |  | D04
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  | X |  | 47 | [5 empty] | X | X | X
2 | X | X | X |  | X |  | X |  | 48 | [5 empty] | X | X | X
3 | X | X | X |  | X |  |  |  | 49 | [5 empty] | X | X
4 | X | X | X |  | X |  |  |  | 50 | [5 empty] | X | X
5 | X | X | X |  | X |  |  |  | 51 | [5 empty] | X | X
6 | X | X | X |  | X |  |  |  | 52 | [5 empty] | X | X
7 | X | X | X |  | X |  |  |  | 53
8 | X | X | X |  | X |  |  |  | 54
9 | X | X | X |  | X |  |  |  | 55
10 | X | X | X |  | X |  |  |  | 56
11 | X | X | X |  | X |  |  |  | 57
12 | X | X | X |  | X |  |  |  | 58
13 | X | X | X |  | X |  |  |  | 59
14 | X | X | X |  | X |  |  |  | 60
15 | X | X | X |  | X |  |  |  | 61
16 | X | X | X |  | X |  |  |  | 62
17 | X | X | X |  | X |  |  |  | 63
18 | X | X | X |  | X |  |  |  | 64
19 | X | X | X |  | X |  |  |  | 65
20 | X | X | X |  | X |  |  |  | 66
21 | X | X | X |  | X |  |  |  | 67
22 | X | X | X |  | X |  |  |  | 68
23 | X | X | X |  | X |  |  |  | 69
24 | X | X | X |  | X |  |  |  | 70
25 | X | X | X |  | X |  |  |  | 71
26 | X | X | X |  | X |  |  |  | 72
27 | X | X | X |  | X |  |  |  | 73
28 | X | X | X |  | X |  |  |  | 74
29 | X | X | X |  | X |  |  |  | 75
30 | X | X | X |  | X |  |  |  | 76
31 | X | X | X |  | X |  |  |  | 77
32 | X | X | X |  | X |  |  |  | 78
33 | X | X | X |  | X |  |  |  | 79
34 | X | X | X |  | X |  |  |  | 80
35 | X | X | X |  | X |  |  |  | 81
36 | X | X | X |  | X |  |  |  | 82
37 | X | X | X |  | X |  |  |  | 83
38 | X | X | X |  | X |  |  |  | 84
39 | X | X | X |  | X |  |  |  | 85
40 |  | X | X |  | X |  |  |  | 86
41 |  | X | X |  | X |  |  |  | 87
42 |  | X | X |  | X |  |  |  | 88
43 |  | X | X |  | X |  |  |  | 89
44 |  | X | X |  | X |  |  |  | 90
45 |  |  | X |  | X |  |  |  | 91
46 |  |  | X |  | X |  |  |  | 92

## BK05
DATA SHEET FOR PHASE CONDUCTOR (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Conductor Name | HYENA
5 | Applicable standard | ASTM B232, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
6 | Max allowable temperature of conductor (°c) | 85
7 | Reted short circuit current for 0.5 Sec. (KA) | 18.8
8 | Max. temperature range (operation) | 75
9 | Temperature range for installation(°c) | -5 ~ +55
10 | Stranding and wire diameter (nos./mm):
11 | Aluminium | 7/4.39
12 | Steel | 7/1.93
13 | Overall diameter(mm) | 14.57
14 | Aluminium Area (mm²) | 106
15 | Steel area (mm²) | 20.48
16 | Total area (mm²) | 126.2
17 | Weight (kg/km):
18 | Aluminium | 290
19 | Steel | 160
20 | Total | 450
21 | Nominal current in 30° (A) | 441
22 | Ultimate tensile Strength (kg) | 4090
23 | Coefficient of linear expansion (1 /C° x 10-6) | 18.8
24 | Initial modulus of elasticity (kg/mm²) | 6000
25 | Final modulus of elasticity (kg/mm²) | 7450
26 | DC resistance at 20°C(Ω/km) | 0.2713
27 | AC resistance at 25°C(Ω/km) | 0.277
28 | AC resistance at 75°C(Ω/km) | 0.3142
29 | Temperature range (transport / storage) | By vendor
30 | Pollution condition | Heavy
31 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR SHIELD WIRE (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Code Name | 7No.8 AWG
5 | Applicable standard | ASTM B416, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
8 | Stranding and wire diameter (nos./mm): | 7/3.26
9 | Overall diameter(mm) | 9.78
10 | Total area (mm²) | 58.43
11 | Weight (kg/km): | 390
12 | Ultimate tensile Strength (kg) | 7226
13 | Coefficient of linear expansion (1 /C° x 10-6) | 13
14 | Initial modulus of elasticity (kg/mm²) | 16000
15 | Final modulus of elasticity (kg/mm²) | 16000
16 | DC resistance at 20°C(Ω/km) | 1.467
17 | Pollution condition | Heavy
18 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR INSULATOR (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | BALL & SOCKET
2 | Applicable Standard | IEC60120, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 426
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material | Porcelain
5 | Nominal line to line voltage rating (kV) | 11
6 | Maximum continuous line to line operating voltage (kV) | 12
7 | Rated frequency (Hz) | 50
8 | Creepage distance (mm/kV) | 31
9 | Minimum creepage distance of insulator (mm) | 372
10 | Minimum mechanical Failing Load (kN) | 70
11 | Socket coupling size (IEC60120) | 16
12 | Ball coupling size (IEC60120) | 16
13 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
14 | Rated lightning impulse withstand voltage across the isolating dist. of Fuse base (kVpeak) | 75
15 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
16 | Rated one minute PF withstand voltage across the isolating dist. of Fuse base (kVrms) | 32
17 | Power Frequency Puncture Voltage (kV) | 110
18 | Metallic Part material | Malleable Cast Iron
19 | Insulator material | Brown Glazed Porcelain
20 | Metallic parts | Malleable cast iron
21 | Washable in service | Yes
22 | Unit Spacing (mm) | By vendor
23 | Disc Diameter (mm) | By vendor
24 | Total Weight | By vendor
25 | Type and Material of Terminal | By vendor
26 | Pollution condition | Heavy
27 | Routine tests & Type test | Acc To IEC 383
DATA SHEET FOR FITTING SUSPENSION & TENSION SET (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | FORGED STEEL
2 | Applicable standard | IEC 61284, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 465
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material: | -
5 | Outer Part | AL.ALLOY
6 | Iner Part | FORGED STEEL, Hot Deep Galvanized.
7 | Jumper Plate | AL.ALLOY
8 | Terminal Jumper | AL.ALLOY
9 | Bolts & Nuts & Washers | STEEL, Hot Deep Galvanized.
10 | Split Pin | STAINLESS STEEL
11 | Min breaking strength | 95% OF CONDUCTOR U.T.S
12 | Coupling Standard IEC | 16 mmA
13 | Short Circuit Current | 25kA/0.4Sec.
14 | Arcing Horn | STEEL
15 | Min breaking strength (KN) | 80
16 | Anti-Climbing Devices and Safety Signs for Lines up to 400kV | ENA TS 43-90
17 | Tower Identification | Steel Sheet with 2mm Thickness
18 | Danger Alarm | Steel Sheet with 1.2mm Thickness
19 | Pollution condition | Heavy
20 | Routine tests & Type test | Acc To IEC 61284
DATA SHEET FOR EARTHING SYSTEM (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | GROUND WIRE :
2 | Type | Copper Conductor
3 | Applicable standard | DIN 48201, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 409
4 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
5 | Stranding (No./mm) | 7/2.5
6 | Total cross section (mm2) | 35
7 | Overall Diameter (mm) | 7.5
8 | Unit Weight (kg/m) | 0.31
9 | Calculated breaking load (kN) | 13.77
10 | DC Resistance At 20°C (ohm/km) | 0.5265
11 | TOWER BONDING CLAMP :
12 | Type of Body | Forged Steel
13 | Surface Coating | HOT DIP. GALV. Acc to ASTM A123 & A153 or BS729
14 | Type of Bolt & Nut | Steel
15 | Torgue on Bolt | 20 NM
16 | Applicable standard | ST37 & DIN931,934,125,127
17 | Diameter of Wire catcher | Ø 8-13 mm
18 | Pollution condition | Heavy
19 | Routine tests & Type test | Acc To DIN 48201
DATA SHEET FOR DISCONNECTOR SWITCH (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Installation (indoor / outdoor) | Outdoor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal system voltage, 3phase | 11 kV
5 | System voltage variation | ± 10%
6 | Nominal frequency and frequency variation | 50 ± 5%
7 | Numbers of poles and current rating | 3pole / 630 A
8 | Short circuit amper and time duration | 25 kA / 1 s
9 | Rated peak withstand current | 62.5 kA
10 | Creepage distance (mm/kV) | 31
11 | Minimum creepage distance of insulator (mm) | 372
12 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
13 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
14 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
15 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
16 | Mode of operation OPEN/CLOSE | open-close manual and with earth blad and earth switch manual
17 | Disconnectors & Earthing switches Operating | Hand operating
18 | Accessories | with earth blad and earth switch manual
19 | Disconnector Mechanism | Center break
20 | Construction | Three pole operation Containing Earthing switch
21 | Ingress protection of electrical enclosures | Min. IP55 (If Needed)
22 | Disconnector status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
23 | Earthing switch status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
24 | Interlocks(Electrical & Mechanical) | To prevent closure of earth switch when Disconnector is not in open position To prevent closure of Disconnector when earth switch is not in open position
25 | Dimensions & weights | By Vendor
26 | Pollution condition | Heavy
27 | Minimum Rating plate data | Manufacturer Type designation and serial number Rated voltage Rated lightning impulse withstand voltage across open pole Rated lightning impulse withstand voltage between poles Rated power frequency withstand voltage across open pole Rated power frequency withstand voltage between poles Rated normal current Rated duration of short circuit Rated no load transformer breaking current Year of manufacture Relevant standard with date of issue
28 | Routine Tests: a) dielectric test on the main circuit (clause 7.1 of IEC60694) b) tests on auxiliary and control circuits (Clause 7.2 of IEC60694) c) measurement of the resistance of the main circuit (Clause 7.3 of IEC60694); d) tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-102 | Witness & Report
29 | Type Tests | Certified Reports of test on the identical type according to IEC62271-102 or IEC129
DATA SHEET FOR CUT OUT FUSE (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Class | Outdoor
2 | Type | Channel Type
3 | Manufacturer of Fuse base & link | By Vendor
4 | Applicable Standard | IEC60282 , IEC60787, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
5 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
6 | Nominal line to line voltage rating (kV) | 11
7 | Maximum continuous line to line operating voltage (kV) | 12
8 | Rated frequency (Hz) | 50
9 | Color of Porcelain insulator | By Vendor
10 | Rated current of Fuse base (A) | 100
11 | Rated current of Fuse link (A) | 10
12 | Creepage distance (mm/kV) | 31
13 | Minimum creepage distance of insulator (mm) | 372
14 | Rated maximum braking current (kA) | 16
15 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
16 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
17 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
18 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
19 | Fuse class | Full-range
20 | Operating pole | Required
21 | Mounting brackets and accessories | Required
22 | Provision for mounting of surge arrester | Required
23 | Weight of Fuse-base & Fuse link | By Vendor
24 | Dimension of Fuse-base | By Vendor
25 | Dimension of Fuse-link | By Vendor
26 | Pollution condition | Heavy
27 | Minimum data required on rating plate | On the fuse base: Manufacturer's name Manufacturer's type designation Rated insulation level Rated voltage Rated current On the fuse carrier: Manufacturer's name Rated voltage Rated current Rated breaking capacity and TRV class Rated frequency On the fuse links: Manufacturer's name Manufacturer's type designation Rated current and speed designation Rated voltage
28 | Routine Tests | Witness and Report according to IEC 60282-2
29 | Type Tests | Certified Report on the identical type according to IEC 60282-2
DATA SHEET FOR LIGHTNING ARRESTER (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | ZnO
2 | Applicable Standard | IEC60099-4, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal line to line voltage rating (kV) | 11
5 | Maximum continuous line to line operating voltage (kV) | 12
6 | Continuous Operating Voltage (Ucov) | 9.6
7 | Rated frequency (Hz) | 50
8 | Material of insulator | By vendor
9 | Earth fault factor | 1.4
10 | Line discharge class per IEC 60099-4 | 2
11 | Minimum energy discharge capability (kJ/kV) U rated | Acc. To IEC
12 | Nominal discharge current with 8/20 microsecond wave (kA peak) | 10
13 | Pressure relief class (kA) | 20
14 | Creepage distance (mm/kV) | 31
15 | Minimum creepage distance of insulator (mm) | 372
16 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
17 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
18 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
19 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
20 | Whether surge counter required? | No
21 | Washable in service | Yes
22 | Temporary overvoltage factor (Ktov) at 1 Sec. at 10 Sec. at 100 Sec. | By vendor
23 | 5kA, 8/20µs lightning impulse protective level | By vendor
24 | 10kA, 8/20µs lightning impulse protective level (Ur 10kA, 8/20) | Residual voltage < 43.2kV
25 | 20kA, 8/20µs lightning impulse protective level | By vendor
26 | 125A, 30/60µs switching impulse protective level | By vendor
27 | Height of Surge Arrester | By vendor
28 | Diameter of Sheds | By vendor
29 | Total Weight of Surge Arrester | By vendor
30 | Type and Material of Terminal | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Manufacturer type designation Serial number Continuous operating voltage Rated voltage Rated frequency Nominal discharge current Pressure relief short time current Line discharge current Pollution degree Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Measurement of reference voltage Uref (Clause 8.1.a of IEC 60099-4) b) Residual voltage test (Clause 8.1.b of IEC 60099-4) c) Internal Partial Discharge test (Clause 8.1.c of IEC 60099-4); d) Leakage test for sealed housing arresters (Clause 8.1.d of IEC 60099-4) e) Design and visual checks acc. to purchase specifications | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 60099-4
DATA SHEET FOR LOAD BREAK SWITCH (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IEC 62271-103, IEC 60694, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type | SF6
5 | Rated Voltage | 11kV
6 | Rated Frequency | 50Hz
7 | No. of Phases and Poles | 3 Phase, 3 Pole
8 | 1 minute power freq. withstand voltage To earth and between phases: Across isolating distance: | 28kV 32kV
9 | Lightning impulse withstand voltage To earth and between phases: Across isolating distance: | 60kV 75kV
10 | Rated Normal Current | 630 A
11 | Mainly active load breaking current | By vendor (> 200A)
12 | Closed loop breaking current | By vendor
13 | Line charging breaking current | By vendor
14 | Cable charging breaking current | By vendor
15 | No load transformer breaking current | By vendor (> 0.74A)
16 | Rated Short Time Withstand Current | 25kA, 3 Sec.
17 | Rated Peak Withstand Current | 62.5kA
18 | Rated Short Circuit Making Current | 62.5kA
19 | Number of breaking operation CO | By vendor
20 | Supporting Structure Material | Hot dipped galvanized steel
21 | Creepage distance (mm/kV) | 31
22 | Min. Creepage Distance of insulators | 372mm
23 | Ingress protection of el. Enclosures | Min. IP55
24 | Operating mechanism | Hand operated mechanism, common for three poles
25 | Permissible tensile force on terminals | By vendor
26 | Gas pressure indicator | Required
27 | Auxiliary Contacts: No. of Make Contacts No. of Break Contacts Rated Voltage Rated Current Breaking Current at 110V DC | By vendor: Min. 4 Min. 4 110V DC Min. 10A Min. 2A
28 | Anti-Condensation Heater | 230V AC, 1Ph, 50Hz
29 | Interlocks with Earth Switch | Load Break Switch + Earth Switch integrated as one unit
30 | Dimensions and Weight | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Type designation and serial number Rated voltage One minute power frequency withstand voltage Lightning impulse withstand voltage Rated normal current Rated short time withstand current Mainly active load breaking current Closed loop breaking current Line charging breaking current Cable charging breaking current No load transformer breaking current Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Dielectric test on the main circuit (Clause 7.1 of IEC 60694) b) Tests on auxiliary and control circuits (Clause 7.2 of IEC 60694) c) Measurement of the resistance of the main circuit (Clause 7.3 of IEC60694) d) Tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-100 | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 62271-103
DATA SHEET FOR TOWER (BK05)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 440
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type of Steel: Analysis of steel Carbon Manganese Sulphur Phosphorus Silicon | MILD High Strength ST 37(235JR) ST 52(355JR) 0.17 0.2 1.4 1.6 0.045 0.05 0.045 0.05 0.3 0.55
5 | Thickness of steel (1.6-3.2mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 65 65 460
6 | Thickness of steel (3.2-4.8mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 75 75 530
7 | Thickness of steel (4.8-6.4mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 85 85 600
8 | Strength in Tension Standard Designation | BS 8100 – Lattice Towers and Masts
9 | Strength in Tension (Ultimate tensile stress) | 340-470 490-630
10 | Strength in Tension (Yield stress) | 235 355
11 | Strength in Compression (Elongation) | 24% 22%
12 | Strength in Compression (Min zinc coating) | 85μ 85μ
13 | Bolts & Nuts Characteristics: Standard designation Steel material Property class Ultimate shearing stress (On bolt shank) Ultimate Bearing stress Min zinc coating | ANSI C 135-1 (Galvanized Steel Bolts and Nuts for Overhead Lines) Steel Steel 5.6 5.8 2100kg/cm2 2800kg/cm2 5400kg/cm2 6000kg/cm2 46μ 46μ
14 | Pollution condition | Heavy
15 | Routine tests & Type test | According to ASCE1090 Manual 52
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 3 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 4 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 5 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 6 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 7 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 8 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 9 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 10 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 11 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 12 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK

## BK12
DATA SHEET FOR PHASE CONDUCTOR (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Conductor Name | HYENA
5 | Applicable standard | ASTM B232, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
6 | Max allowable temperature of conductor (°c) | 85
7 | Reted short circuit current for 0.5 Sec. (KA) | 18.8
8 | Max. temperature range (operation) | 75
9 | Temperature range for installation(°c) | -5 ~ +55
10 | Stranding and wire diameter (nos./mm):
11 | Aluminium | 7/4.39
12 | Steel | 7/1.93
13 | Overall diameter(mm) | 14.57
14 | Aluminium Area (mm²) | 106
15 | Steel area (mm²) | 20.48
16 | Total area (mm²) | 126.2
17 | Weight (kg/km):
18 | Aluminium | 290
19 | Steel | 160
20 | Total | 450
21 | Nominal current in 30° (A) | 441
22 | Ultimate tensile Strength (kg) | 4090
23 | Coefficient of linear expansion (1 /C° x 10-6) | 18.8
24 | Initial modulus of elasticity (kg/mm²) | 6000
25 | Final modulus of elasticity (kg/mm²) | 7450
26 | DC resistance at 20°C(Ω/km) | 0.2713
27 | AC resistance at 25°C(Ω/km) | 0.277
28 | AC resistance at 75°C(Ω/km) | 0.3142
29 | Temperature range (transport / storage) | By vendor
30 | Pollution condition | Heavy
31 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR SHIELD WIRE (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Code Name | 7No.8 AWG
5 | Applicable standard | ASTM B416, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
8 | Stranding and wire diameter (nos./mm): | 7/3.26
9 | Overall diameter(mm) | 9.78
10 | Total area (mm²) | 58.43
11 | Weight (kg/km): | 390
12 | Ultimate tensile Strength (kg) | 7226
13 | Coefficient of linear expansion (1 /C° x 10-6) | 13
14 | Initial modulus of elasticity (kg/mm²) | 16000
15 | Final modulus of elasticity (kg/mm²) | 16000
16 | DC resistance at 20°C(Ω/km) | 1.467
17 | Pollution condition | Heavy
18 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR INSULATOR (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | BALL & SOCKET
2 | Applicable Standard | IEC60120, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 426
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material | Porcelain
5 | Nominal line to line voltage rating (kV) | 11
6 | Maximum continuous line to line operating voltage (kV) | 12
7 | Rated frequency (Hz) | 50
8 | Creepage distance (mm/kV) | 31
9 | Minimum creepage distance of insulator (mm) | 372
10 | Minimum mechanical Failing Load (kN) | 70
11 | Socket coupling size (IEC60120) | 16
12 | Ball coupling size (IEC60120) | 16
13 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
14 | Rated lightning impulse withstand voltage across the isolating dist. of Fuse base (kVpeak) | 75
15 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
16 | Rated one minute PF withstand voltage across the isolating dist. of Fuse base (kVrms) | 32
17 | Power Frequency Puncture Voltage (kV) | 110
18 | Metallic Part material | Malleable Cast Iron
19 | Insulator material | Brown Glazed Porcelain
20 | Metallic parts | Malleable cast iron
21 | Washable in service | Yes
22 | Unit Spacing (mm) | By vendor
23 | Disc Diameter (mm) | By vendor
24 | Total Weight | By vendor
25 | Type and Material of Terminal | By vendor
26 | Pollution condition | Heavy
27 | Routine tests & Type test | Acc To IEC 383
DATA SHEET FOR FITTING SUSPENSION & TENSION SET (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | FORGED STEEL
2 | Applicable standard | IEC 61284, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 465
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material: | -
5 | Outer Part | AL.ALLOY
6 | Iner Part | FORGED STEEL, Hot Deep Galvanized.
7 | Jumper Plate | AL.ALLOY
8 | Terminal Jumper | AL.ALLOY
9 | Bolts & Nuts & Washers | STEEL, Hot Deep Galvanized.
10 | Split Pin | STAINLESS STEEL
11 | Min breaking strength | 95% OF CONDUCTOR U.T.S
12 | Coupling Standard IEC | 16 mmA
13 | Short Circuit Current | 25kA/0.4Sec.
14 | Arcing Horn | STEEL
15 | Min breaking strength (KN) | 80
16 | Anti-Climbing Devices and Safety Signs for Lines up to 400kV | ENA TS 43-90
17 | Tower Identification | Steel Sheet with 2mm Thickness
18 | Danger Alarm | Steel Sheet with 1.2mm Thickness
19 | Pollution condition | Heavy
20 | Routine tests & Type test | Acc To IEC 61284
DATA SHEET FOR EARTHING SYSTEM (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | GROUND WIRE :
2 | Type | Copper Conductor
3 | Applicable standard | DIN 48201, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 409
4 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
5 | Stranding (No./mm) | 7/2.5
6 | Total cross section (mm2) | 35
7 | Overall Diameter (mm) | 7.5
8 | Unit Weight (kg/m) | 0.31
9 | Calculated breaking load (kN) | 13.77
10 | DC Resistance At 20°C (ohm/km) | 0.5265
11 | TOWER BONDING CLAMP :
12 | Type of Body | Forged Steel
13 | Surface Coating | HOT DIP. GALV. Acc to ASTM A123 & A153 or BS729
14 | Type of Bolt & Nut | Steel
15 | Torgue on Bolt | 20 NM
16 | Applicable standard | ST37 & DIN931,934,125,127
17 | Diameter of Wire catcher | Ø 8-13 mm
18 | Pollution condition | Heavy
19 | Routine tests & Type test | Acc To DIN 48201
DATA SHEET FOR DISCONNECTOR SWITCH (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Installation (indoor / outdoor) | Outdoor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal system voltage, 3phase | 11 kV
5 | System voltage variation | ± 10%
6 | Nominal frequency and frequency variation | 50 ± 5%
7 | Numbers of poles and current rating | 3pole / 630 A
8 | Short circuit amper and time duration | 25 kA / 1 s
9 | Rated peak withstand current | 62.5 kA
10 | Creepage distance (mm/kV) | 31
11 | Minimum creepage distance of insulator (mm) | 372
12 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
13 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
14 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
15 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
16 | Mode of operation OPEN/CLOSE | open-close manual and with earth blad and earth switch manual
17 | Disconnectors & Earthing switches Operating | Hand operating
18 | Accessories | with earth blad and earth switch manual
19 | Disconnector Mechanism | Center break
20 | Construction | Three pole operation Containing Earthing switch
21 | Ingress protection of electrical enclosures | Min. IP55 (If Needed)
22 | Disconnector status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
23 | Earthing switch status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
24 | Interlocks(Electrical & Mechanical) | To prevent closure of earth switch when Disconnector is not in open position To prevent closure of Disconnector when earth switch is not in open position
25 | Dimensions & weights | By Vendor
26 | Pollution condition | Heavy
27 | Minimum Rating plate data | Manufacturer Type designation and serial number Rated voltage Rated lightning impulse withstand voltage across open pole Rated lightning impulse withstand voltage between poles Rated power frequency withstand voltage across open pole Rated power frequency withstand voltage between poles Rated normal current Rated duration of short circuit Rated no load transformer breaking current Year of manufacture Relevant standard with date of issue
28 | Routine Tests: a) dielectric test on the main circuit (clause 7.1 of IEC60694) b) tests on auxiliary and control circuits (Clause 7.2 of IEC60694) c) measurement of the resistance of the main circuit (Clause 7.3 of IEC60694); d) tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-102 | Witness & Report
29 | Type Tests | Certified Reports of test on the identical type according to IEC62271-102 or IEC129
DATA SHEET FOR CUT OUT FUSE (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Class | Outdoor
2 | Type | Channel Type
3 | Manufacturer of Fuse base & link | By Vendor
4 | Applicable Standard | IEC60282 , IEC60787, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
5 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
6 | Nominal line to line voltage rating (kV) | 11
7 | Maximum continuous line to line operating voltage (kV) | 12
8 | Rated frequency (Hz) | 50
9 | Color of Porcelain insulator | By Vendor
10 | Rated current of Fuse base (A) | 100
11 | Rated current of Fuse link (A) | 10
12 | Creepage distance (mm/kV) | 31
13 | Minimum creepage distance of insulator (mm) | 372
14 | Rated maximum braking current (kA) | 16
15 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
16 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
17 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
18 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
19 | Fuse class | Full-range
20 | Operating pole | Required
21 | Mounting brackets and accessories | Required
22 | Provision for mounting of surge arrester | Required
23 | Weight of Fuse-base & Fuse link | By Vendor
24 | Dimension of Fuse-base | By Vendor
25 | Dimension of Fuse-link | By Vendor
26 | Pollution condition | Heavy
27 | Minimum data required on rating plate | On the fuse base: Manufacturer's name Manufacturer's type designation Rated insulation level Rated voltage Rated current On the fuse carrier: Manufacturer's name Rated voltage Rated current Rated breaking capacity and TRV class Rated frequency On the fuse links: Manufacturer's name Manufacturer's type designation Rated current and speed designation Rated voltage
28 | Routine Tests | Witness and Report according to IEC 60282-2
29 | Type Tests | Certified Report on the identical type according to IEC 60282-2
DATA SHEET FOR LIGHTNING ARRESTER (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | ZnO
2 | Applicable Standard | IEC60099-4, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal line to line voltage rating (kV) | 11
5 | Maximum continuous line to line operating voltage (kV) | 12
6 | Continuous Operating Voltage (Ucov) | 9.6
7 | Rated frequency (Hz) | 50
8 | Material of insulator | By vendor
9 | Earth fault factor | 1.4
10 | Line discharge class per IEC 60099-4 | 2
11 | Minimum energy discharge capability (kJ/kV) U rated | Acc. To IEC
12 | Nominal discharge current with 8/20 microsecond wave (kA peak) | 10
13 | Pressure relief class (kA) | 20
14 | Creepage distance (mm/kV) | 31
15 | Minimum creepage distance of insulator (mm) | 372
16 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
17 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
18 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
19 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
20 | Whether surge counter required? | No
21 | Washable in service | Yes
22 | Temporary overvoltage factor (Ktov) at 1 Sec. at 10 Sec. at 100 Sec. | By vendor
23 | 5kA, 8/20µs lightning impulse protective level | By vendor
24 | 10kA, 8/20µs lightning impulse protective level (Ur 10kA, 8/20) | Residual voltage < 43.2kV
25 | 20kA, 8/20µs lightning impulse protective level | By vendor
26 | 125A, 30/60µs switching impulse protective level | By vendor
27 | Height of Surge Arrester | By vendor
28 | Diameter of Sheds | By vendor
29 | Total Weight of Surge Arrester | By vendor
30 | Type and Material of Terminal | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Manufacturer type designation Serial number Continuous operating voltage Rated voltage Rated frequency Nominal discharge current Pressure relief short time current Line discharge current Pollution degree Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Measurement of reference voltage Uref (Clause 8.1.a of IEC 60099-4) b) Residual voltage test (Clause 8.1.b of IEC 60099-4) c) Internal Partial Discharge test (Clause 8.1.c of IEC 60099-4); d) Leakage test for sealed housing arresters (Clause 8.1.d of IEC 60099-4) e) Design and visual checks acc. to purchase specifications | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 60099-4
DATA SHEET FOR LOAD BREAK SWITCH (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IEC 62271-103, IEC 60694, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type | SF6
5 | Rated Voltage | 11kV
6 | Rated Frequency | 50Hz
7 | No. of Phases and Poles | 3 Phase, 3 Pole
8 | 1 minute power freq. withstand voltage To earth and between phases: Across isolating distance: | 28kV 32kV
9 | Lightning impulse withstand voltage To earth and between phases: Across isolating distance: | 60kV 75kV
10 | Rated Normal Current | 630 A
11 | Mainly active load breaking current | By vendor (> 200A)
12 | Closed loop breaking current | By vendor
13 | Line charging breaking current | By vendor
14 | Cable charging breaking current | By vendor
15 | No load transformer breaking current | By vendor (> 0.74A)
16 | Rated Short Time Withstand Current | 25kA, 3 Sec.
17 | Rated Peak Withstand Current | 62.5kA
18 | Rated Short Circuit Making Current | 62.5kA
19 | Number of breaking operation CO | By vendor
20 | Supporting Structure Material | Hot dipped galvanized steel
21 | Creepage distance (mm/kV) | 31
22 | Min. Creepage Distance of insulators | 372mm
23 | Ingress protection of el. Enclosures | Min. IP55
24 | Operating mechanism | Hand operated mechanism, common for three poles
25 | Permissible tensile force on terminals | By vendor
26 | Gas pressure indicator | Required
27 | Auxiliary Contacts: No. of Make Contacts No. of Break Contacts Rated Voltage Rated Current Breaking Current at 110V DC | By vendor: Min. 4 Min. 4 110V DC Min. 10A Min. 2A
28 | Anti-Condensation Heater | 230V AC, 1Ph, 50Hz
29 | Interlocks with Earth Switch | Load Break Switch + Earth Switch integrated as one unit
30 | Dimensions and Weight | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Type designation and serial number Rated voltage One minute power frequency withstand voltage Lightning impulse withstand voltage Rated normal current Rated short time withstand current Mainly active load breaking current Closed loop breaking current Line charging breaking current Cable charging breaking current No load transformer breaking current Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Dielectric test on the main circuit (Clause 7.1 of IEC 60694) b) Tests on auxiliary and control circuits (Clause 7.2 of IEC 60694) c) Measurement of the resistance of the main circuit (Clause 7.3 of IEC60694) d) Tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-100 | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 62271-103
DATA SHEET FOR TOWER (BK12)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 440
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type of Steel: Analysis of steel Carbon Manganese Sulphur Phosphorus Silicon | MILD High Strength ST 37(235JR) ST 52(355JR) 0.17 0.2 1.4 1.6 0.045 0.05 0.045 0.05 0.3 0.55
5 | Thickness of steel (1.6-3.2mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 65 65 460
6 | Thickness of steel (3.2-4.8mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 75 75 530
7 | Thickness of steel (4.8-6.4mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 85 85 600
8 | Strength in Tension Standard Designation | BS 8100 – Lattice Towers and Masts
9 | Strength in Tension (Ultimate tensile stress) | 340-470 490-630
10 | Strength in Tension (Yield stress) | 235 355
11 | Strength in Compression (Elongation) | 24% 22%
12 | Strength in Compression (Min zinc coating) | 85μ 85μ
13 | Bolts & Nuts Characteristics: Standard designation Steel material Property class Ultimate shearing stress (On bolt shank) Ultimate Bearing stress Min zinc coating | ANSI C 135-1 (Galvanized Steel Bolts and Nuts for Overhead Lines) Steel Steel 5.6 5.8 2100kg/cm2 2800kg/cm2 5400kg/cm2 6000kg/cm2 46μ 46μ
14 | Pollution condition | Heavy
15 | Routine tests & Type test | According to ASCE1090 Manual 52
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 13 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 14 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 15 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 16 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 17 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 18 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 19 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 20 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 21 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 22 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK

## BK15
DATA SHEET FOR PHASE CONDUCTOR (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Conductor Name | HYENA
5 | Applicable standard | ASTM B232, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
6 | Max allowable temperature of conductor (°c) | 85
7 | Reted short circuit current for 0.5 Sec. (KA) | 18.8
8 | Max. temperature range (operation) | 75
9 | Temperature range for installation(°c) | -5 ~ +55
10 | Stranding and wire diameter (nos./mm):
11 | Aluminium | 7/4.39
12 | Steel | 7/1.93
13 | Overall diameter(mm) | 14.57
14 | Aluminium Area (mm²) | 106
15 | Steel area (mm²) | 20.48
16 | Total area (mm²) | 126.2
17 | Weight (kg/km):
18 | Aluminium | 290
19 | Steel | 160
20 | Total | 450
21 | Nominal current in 30° (A) | 441
22 | Ultimate tensile Strength (kg) | 4090
23 | Coefficient of linear expansion (1 /C° x 10-6) | 18.8
24 | Initial modulus of elasticity (kg/mm²) | 6000
25 | Final modulus of elasticity (kg/mm²) | 7450
26 | DC resistance at 20°C(Ω/km) | 0.2713
27 | AC resistance at 25°C(Ω/km) | 0.277
28 | AC resistance at 75°C(Ω/km) | 0.3142
29 | Temperature range (transport / storage) | By vendor
30 | Pollution condition | Heavy
31 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR SHIELD WIRE (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Code Name | 7No.8 AWG
5 | Applicable standard | ASTM B416, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
8 | Stranding and wire diameter (nos./mm): | 7/3.26
9 | Overall diameter(mm) | 9.78
10 | Total area (mm²) | 58.43
11 | Weight (kg/km): | 390
12 | Ultimate tensile Strength (kg) | 7226
13 | Coefficient of linear expansion (1 /C° x 10-6) | 13
14 | Initial modulus of elasticity (kg/mm²) | 16000
15 | Final modulus of elasticity (kg/mm²) | 16000
16 | DC resistance at 20°C(Ω/km) | s
17 | Pollution condition | Heavy
18 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR INSULATOR (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | BALL & SOCKET
2 | Applicable Standard | IEC60120, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 426
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material | Porcelain
5 | Nominal line to line voltage rating (kV) | 11
6 | Maximum continuous line to line operating voltage (kV) | 12
7 | Rated frequency (Hz) | 50
8 | Creepage distance (mm/kV) | 31
9 | Minimum creepage distance of insulator (mm) | 372
10 | Minimum mechanical Failing Load (kN) | 70
11 | Socket coupling size (IEC60120) | 16
12 | Ball coupling size (IEC60120) | 16
13 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
14 | Rated lightning impulse withstand voltage across the isolating dist. of Fuse base (kVpeak) | 75
15 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
16 | Rated one minute PF withstand voltage across the isolating dist. of Fuse base (kVrms) | 32
17 | Power Frequency Puncture Voltage (kV) | 110
18 | Metallic Part material | Malleable Cast Iron
19 | Insulator material | Brown Glazed Porcelain
20 | Metallic parts | Malleable cast iron
21 | Washable in service | Yes
22 | Unit Spacing (mm) | By vendor
23 | Disc Diameter (mm) | By vendor
24 | Total Weight | By vendor
25 | Type and Material of Terminal | By vendor
26 | Pollution condition | Heavy
27 | Routine tests & Type test | Acc To IEC 383
DATA SHEET FOR FITTING SUSPENSION & TENSION SET (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | FORGED STEEL
2 | Applicable standard | IEC 61284, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 465
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material: | -
5 | Outer Part | AL.ALLOY
6 | Iner Part | FORGED STEEL, Hot Deep Galvanized.
7 | Jumper Plate | AL.ALLOY
8 | Terminal Jumper | AL.ALLOY
9 | Bolts & Nuts & Washers | STEEL, Hot Deep Galvanized.
10 | Split Pin | STAINLESS STEEL
11 | Min breaking strength | 95% OF CONDUCTOR U.T.S
12 | Coupling Standard IEC | 16 mmA
13 | Short Circuit Current | 25kA/0.4Sec.
14 | Arcing Horn | STEEL
15 | Min breaking strength (KN) | 80
16 | Anti-Climbing Devices and Safety Signs for Lines up to 400kV | ENA TS 43-90
17 | Tower Identification | Steel Sheet with 2mm Thickness
18 | Danger Alarm | Steel Sheet with 1.2mm Thickness
19 | Pollution condition | Heavy
20 | Routine tests & Type test | Acc To IEC 61284
DATA SHEET FOR EARTHING SYSTEM (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | GROUND WIRE :
2 | Type | Copper Conductor
3 | Applicable standard | DIN 48201, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 409
4 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
5 | Stranding (No./mm) | 7/2.5
6 | Total cross section (mm2) | 35
7 | Overall Diameter (mm) | 7.5
8 | Unit Weight (kg/m) | 0.31
9 | Calculated breaking load (kN) | 13.77
10 | DC Resistance At 20°C (ohm/km) | 0.5265
11 | TOWER BONDING CLAMP :
12 | Type of Body | Forged Steel
13 | Surface Coating | HOT DIP. GALV. Acc to ASTM A123 & A153 or BS729
14 | Type of Bolt & Nut | Steel
15 | Torgue on Bolt | 20 NM
16 | Applicable standard | ST37 & DIN931,934,125,127
17 | Diameter of Wire catcher | Ø 8-13 mm
18 | Pollution condition | Heavy
19 | Routine tests & Type test | Acc To DIN 48201
DATA SHEET FOR DISCONNECTOR SWITCH (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Installation (indoor / outdoor) | Outdoor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal system voltage, 3phase | 11 kV
5 | System voltage variation | ± 10%
6 | Nominal frequency and frequency variation | 50 ± 5%
7 | Numbers of poles and current rating | 3pole / 630 A
8 | Short circuit amper and time duration | 25 kA / 1 s
9 | Rated peak withstand current | 62.5 kA
10 | Creepage distance (mm/kV) | 31
11 | Minimum creepage distance of insulator (mm) | 372
12 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
13 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
14 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
15 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
16 | Mode of operation OPEN/CLOSE | open-close manual and with earth blad and earth switch manual
17 | Disconnectors & Earthing switches Operating | Hand operating
18 | Accessories | with earth blad and earth switch manual
19 | Disconnector Mechanism | Center break
20 | Construction | Three pole operation Containing Earthing switch
21 | Ingress protection of electrical enclosures | Min. IP55 (If Needed)
22 | Disconnector status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
23 | Earthing switch status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
24 | Interlocks(Electrical & Mechanical) | To prevent closure of earth switch when Disconnector is not in open position To prevent closure of Disconnector when earth switch is not in open position
25 | Dimensions & weights | By Vendor
26 | Pollution condition | Heavy
27 | Minimum Rating plate data | Manufacturer Type designation and serial number Rated voltage Rated lightning impulse withstand voltage across open pole Rated lightning impulse withstand voltage between poles Rated power frequency withstand voltage across open pole Rated power frequency withstand voltage between poles Rated normal current Rated duration of short circuit Rated no load transformer breaking current Year of manufacture Relevant standard with date of issue
28 | Routine Tests: a) dielectric test on the main circuit (clause 7.1 of IEC60694) b) tests on auxiliary and control circuits (Clause 7.2 of IEC60694) c) measurement of the resistance of the main circuit (Clause 7.3 of IEC60694); d) tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-102 | Witness & Report
29 | Type Tests | Certified Reports of test on the identical type according to IEC62271-102 or IEC129
DATA SHEET FOR CUT OUT FUSE (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Class | Outdoor
2 | Type | Channel Type
3 | Manufacturer of Fuse base & link | By Vendor
4 | Applicable Standard | IEC60282 , IEC60787, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
5 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
6 | Nominal line to line voltage rating (kV) | 11
7 | Maximum continuous line to line operating voltage (kV) | 12
8 | Rated frequency (Hz) | 50
9 | Color of Porcelain insulator | By Vendor
10 | Rated current of Fuse base (A) | 100
11 | Rated current of Fuse link (A) | 10
12 | Creepage distance (mm/kV) | 31
13 | Minimum creepage distance of insulator (mm) | 372
14 | Rated maximum braking current (kA) | 16
15 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
16 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
17 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
18 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
19 | Fuse class | Full-range
20 | Operating pole | Required
21 | Mounting brackets and accessories | Required
22 | Provision for mounting of surge arrester | Required
23 | Weight of Fuse-base & Fuse link | By Vendor
24 | Dimension of Fuse-base | By Vendor
25 | Dimension of Fuse-link | By Vendor
26 | Pollution condition | Heavy
27 | Minimum data required on rating plate | On the fuse base: Manufacturer's name Manufacturer's type designation Rated insulation level Rated voltage Rated current On the fuse carrier: Manufacturer's name Rated voltage Rated current Rated breaking capacity and TRV class Rated frequency On the fuse links: Manufacturer's name Manufacturer's type designation Rated current and speed designation Rated voltage
28 | Routine Tests | Witness and Report according to IEC 60282-2
29 | Type Tests | Certified Report on the identical type according to IEC 60282-2
DATA SHEET FOR LIGHTNING ARRESTER (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | ZnO
2 | Applicable Standard | IEC60099-4, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal line to line voltage rating (kV) | 11
5 | Maximum continuous line to line operating voltage (kV) | 12
6 | Continuous Operating Voltage (Ucov) | 9.6
7 | Rated frequency (Hz) | 50
8 | Material of insulator | By vendor
9 | Earth fault factor | 1.4
10 | Line discharge class per IEC 60099-4 | 2
11 | Minimum energy discharge capability (kJ/kV) U rated | Acc. To IEC
12 | Nominal discharge current with 8/20 microsecond wave (kA peak) | 10
13 | Pressure relief class (kA) | 20
14 | Creepage distance (mm/kV) | 31
15 | Minimum creepage distance of insulator (mm) | 372
16 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
17 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
18 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
19 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
20 | Whether surge counter required? | No
21 | Washable in service | Yes
22 | Temporary overvoltage factor (Ktov) at 1 Sec. at 10 Sec. at 100 Sec. | By vendor
23 | 5kA, 8/20µs lightning impulse protective level | By vendor
24 | 10kA, 8/20µs lightning impulse protective level (Ur 10kA, 8/20) | Residual voltage < 43.2kV
25 | 20kA, 8/20µs lightning impulse protective level | By vendor
26 | 125A, 30/60µs switching impulse protective level | By vendor
27 | Height of Surge Arrester | By vendor
28 | Diameter of Sheds | By vendor
29 | Total Weight of Surge Arrester | By vendor
30 | Type and Material of Terminal | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Manufacturer type designation Serial number Continuous operating voltage Rated voltage Rated frequency Nominal discharge current Pressure relief short time current Line discharge current Pollution degree Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Measurement of reference voltage Uref (Clause 8.1.a of IEC 60099-4) b) Residual voltage test (Clause 8.1.b of IEC 60099-4) c) Internal Partial Discharge test (Clause 8.1.c of IEC 60099-4); d) Leakage test for sealed housing arresters (Clause 8.1.d of IEC 60099-4) e) Design and visual checks acc. to purchase specifications | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 60099-4
DATA SHEET FOR LOAD BREAK SWITCH (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IEC 62271-103, IEC 60694, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type | SF6
5 | Rated Voltage | 11kV
6 | Rated Frequency | 50Hz
7 | No. of Phases and Poles | 3 Phase, 3 Pole
8 | 1 minute power freq. withstand voltage To earth and between phases: Across isolating distance: | 28kV 32kV
9 | Lightning impulse withstand voltage To earth and between phases: Across isolating distance: | 60kV 75kV
10 | Rated Normal Current | 630 A
11 | Mainly active load breaking current | By vendor (> 200A)
12 | Closed loop breaking current | By vendor
13 | Line charging breaking current | By vendor
14 | Cable charging breaking current | By vendor
15 | No load transformer breaking current | By vendor (> 0.74A)
16 | Rated Short Time Withstand Current | 25kA, 3 Sec.
17 | Rated Peak Withstand Current | 62.5kA
18 | Rated Short Circuit Making Current | 62.5kA
19 | Number of breaking operation CO | By vendor
20 | Supporting Structure Material | Hot dipped galvanized steel
21 | Creepage distance (mm/kV) | 31
22 | Min. Creepage Distance of insulators | 372mm
23 | Ingress protection of el. Enclosures | Min. IP55
24 | Operating mechanism | Hand operated mechanism, common for three poles
25 | Permissible tensile force on terminals | By vendor
26 | Gas pressure indicator | Required
27 | Auxiliary Contacts: No. of Make Contacts No. of Break Contacts Rated Voltage Rated Current Breaking Current at 110V DC | By vendor: Min. 4 Min. 4 110V DC Min. 10A Min. 2A
28 | Anti-Condensation Heater | 230V AC, 1Ph, 50Hz
29 | Interlocks with Earth Switch | Load Break Switch + Earth Switch integrated as one unit
30 | Dimensions and Weight | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Type designation and serial number Rated voltage One minute power frequency withstand voltage Lightning impulse withstand voltage Rated normal current Rated short time withstand current Mainly active load breaking current Closed loop breaking current Line charging breaking current Cable charging breaking current No load transformer breaking current Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Dielectric test on the main circuit (Clause 7.1 of IEC 60694) b) Tests on auxiliary and control circuits (Clause 7.2 of IEC 60694) c) Measurement of the resistance of the main circuit (Clause 7.3 of IEC60694) d) Tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-100 | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 62271-103
DATA SHEET FOR TOWER (BK15)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 440
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type of Steel: Analysis of steel Carbon Manganese Sulphur Phosphorus Silicon | MILD High Strength ST 37(235JR) ST 52(355JR) 0.17 0.2 1.4 1.6 0.045 0.05 0.045 0.05 0.3 0.55
5 | Thickness of steel (1.6-3.2mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 65 65 460
6 | Thickness of steel (3.2-4.8mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 75 75 530
7 | Thickness of steel (4.8-6.4mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 85 85 600
8 | Strength in Tension Standard Designation | BS 8100 – Lattice Towers and Masts
9 | Strength in Tension (Ultimate tensile stress) | 340-470 490-630
10 | Strength in Tension (Yield stress) | 235 355
11 | Strength in Compression (Elongation) | 24% 22%
12 | Strength in Compression (Min zinc coating) | 85μ 85μ
13 | Bolts & Nuts Characteristics: Standard designation Steel material Property class Ultimate shearing stress (On bolt shank) Ultimate Bearing stress Min zinc coating | ANSI C 135-1 (Galvanized Steel Bolts and Nuts for Overhead Lines) Steel Steel 5.6 5.8 2100kg/cm2 2800kg/cm2 5400kg/cm2 6000kg/cm2 46μ 46μ
14 | Pollution condition | Heavy
15 | Routine tests & Type test | According to ASCE1090 Manual 52
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 23 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 24 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 25 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 26 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 27 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 28 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 29 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 30 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 31 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 32 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK

## W007S
DATA SHEET FOR PHASE CONDUCTOR (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Conductor Name | HYENA
5 | Applicable standard | ASTM B232, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
6 | Max allowable temperature of conductor (°c) | 85
7 | Reted short circuit current for 0.5 Sec. (KA) | 18.8
8 | Max. temperature range (operation) | 75
9 | Temperature range for installation(°c) | -5 ~ +55
10 | Stranding and wire diameter (nos./mm):
11 | Aluminium | 7/4.39
12 | Steel | 7/1.93
13 | Overall diameter(mm) | 14.57
14 | Aluminium Area (mm²) | 106
15 | Steel area (mm²) | 20.48
16 | Total area (mm²) | 126.2
17 | Weight (kg/km):
18 | Aluminium | 290
19 | Steel | 160
20 | Total | 450
21 | Nominal current in 30° (A) | 441
22 | Ultimate tensile Strength (kg) | 4090
23 | Coefficient of linear expansion (1 /C° x 10-6) | 18.8
24 | Initial modulus of elasticity (kg/mm²) | 6000
25 | Final modulus of elasticity (kg/mm²) | 7450
26 | DC resistance at 20°C(Ω/km) | 0.2713
27 | AC resistance at 25°C(Ω/km) | 0.277
28 | AC resistance at 75°C(Ω/km) | 0.3142
29 | Temperature range (transport / storage) | By vendor
30 | Pollution condition | Heavy
31 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR SHIELD WIRE (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Code Name | 7No.8 AWG
5 | Applicable standard | ASTM B416, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
8 | Stranding and wire diameter (nos./mm): | 7/3.26
9 | Overall diameter(mm) | 9.78
10 | Total area (mm²) | 58.43
11 | Weight (kg/km): | 390
12 | Ultimate tensile Strength (kg) | 7226
13 | Coefficient of linear expansion (1 /C° x 10-6) | 13
14 | Initial modulus of elasticity (kg/mm²) | 16000
15 | Final modulus of elasticity (kg/mm²) | 16000
16 | DC resistance at 20°C(Ω/km) | 1.467
17 | Pollution condition | Heavy
18 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR INSULATOR (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | BALL & SOCKET
2 | Applicable Standard | IEC60120, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 426
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material | Porcelain
5 | Nominal line to line voltage rating (kV) | 11
6 | Maximum continuous line to line operating voltage (kV) | 12
7 | Rated frequency (Hz) | 50
8 | Creepage distance (mm/kV) | 31
9 | Minimum creepage distance of insulator (mm) | 372
10 | Minimum mechanical Failing Load (kN) | 70
11 | Socket coupling size (IEC60120) | 16
12 | Ball coupling size (IEC60120) | 16
13 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
14 | Rated lightning impulse withstand voltage across the isolating dist. of Fuse base (kVpeak) | 75
15 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
16 | Rated one minute PF withstand voltage across the isolating dist. of Fuse base (kVrms) | 32
17 | Power Frequency Puncture Voltage (kV) | 110
18 | Metallic Part material | Malleable Cast Iron
19 | Insulator material | Brown Glazed Porcelain
20 | Metallic parts | Malleable cast iron
21 | Washable in service | Yes
22 | Unit Spacing (mm) | By vendor
23 | Disc Diameter (mm) | By vendor
24 | Total Weight | By vendor
25 | Type and Material of Terminal | By vendor
26 | Pollution condition | Heavy
27 | Routine tests & Type test | Acc To IEC 383
DATA SHEET FOR FITTING SUSPENSION & TENSION SET (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | FORGED STEEL
2 | Applicable standard | IEC 61284, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 465
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material: | -
5 | Outer Part | AL.ALLOY
6 | Iner Part | FORGED STEEL, Hot Deep Galvanized.
7 | Jumper Plate | AL.ALLOY
8 | Terminal Jumper | AL.ALLOY
9 | Bolts & Nuts & Washers | STEEL, Hot Deep Galvanized.
10 | Split Pin | STAINLESS STEEL
11 | Min breaking strength | 95% OF CONDUCTOR U.T.S
12 | Coupling Standard IEC | 16 mmA
13 | Short Circuit Current | 25kA/0.4Sec.
14 | Arcing Horn | STEEL
15 | Min breaking strength (KN) | 80
16 | Anti-Climbing Devices and Safety Signs for Lines up to 400kV | ENA TS 43-90
17 | Tower Identification | Steel Sheet with 2mm Thickness
18 | Danger Alarm | Steel Sheet with 1.2mm Thickness
19 | Pollution condition | Heavy
20 | Routine tests & Type test | Acc To IEC 61284
DATA SHEET FOR EARTHING SYSTEM (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | GROUND WIRE :
2 | Type | Copper Conductor
3 | Applicable standard | DIN 48201, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 409
4 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
5 | Stranding (No./mm) | 7/2.5
6 | Total cross section (mm2) | 35
7 | Overall Diameter (mm) | 7.5
8 | Unit Weight (kg/m) | 0.31
9 | Calculated breaking load (kN) | 13.77
10 | DC Resistance At 20°C (ohm/km) | 0.5265
11 | TOWER BONDING CLAMP :
12 | Type of Body | Forged Steel
13 | Surface Coating | HOT DIP. GALV. Acc to ASTM A123 & A153 or BS729
14 | Type of Bolt & Nut | Steel
15 | Torgue on Bolt | 20 NM
16 | Applicable standard | ST37 & DIN931,934,125,127
17 | Diameter of Wire catcher | Ø 8-13 mm
18 | Pollution condition | Heavy
19 | Routine tests & Type test | Acc To DIN 48201
DATA SHEET FOR DISCONNECTOR SWITCH (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Installation (indoor / outdoor) | Outdoor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal system voltage, 3phase | 11 kV
5 | System voltage variation | ± 10%
6 | Nominal frequency and frequency variation | 50 ± 5%
7 | Numbers of poles and current rating | 3pole / 630 A
8 | Short circuit amper and time duration | 25 kA / 1 s
9 | Rated peak withstand current | 62.5 kA
10 | Creepage distance (mm/kV) | 31
11 | Minimum creepage distance of insulator (mm) | 372
12 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
13 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
14 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
15 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
16 | Mode of operation OPEN/CLOSE | open-close manual and with earth blad and earth switch manual
17 | Disconnectors & Earthing switches Operating | Hand operating
18 | Accessories | with earth blad and earth switch manual
19 | Disconnector Mechanism | Center break
20 | Construction | Three pole operation Containing Earthing switch
21 | Ingress protection of electrical enclosures | Min. IP55 (If Needed)
22 | Disconnector status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
23 | Earthing switch status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
24 | Interlocks(Electrical & Mechanical) | To prevent closure of earth switch when Disconnector is not in open position To prevent closure of Disconnector when earth switch is not in open position
25 | Dimensions & weights | By Vendor
26 | Pollution condition | Heavy
27 | Minimum Rating plate data | Manufacturer Type designation and serial number Rated voltage Rated lightning impulse withstand voltage across open pole Rated lightning impulse withstand voltage between poles Rated power frequency withstand voltage across open pole Rated power frequency withstand voltage between poles Rated normal current Rated duration of short circuit Rated no load transformer breaking current Year of manufacture Relevant standard with date of issue
28 | Routine Tests: a) dielectric test on the main circuit (clause 7.1 of IEC60694) b) tests on auxiliary and control circuits (Clause 7.2 of IEC60694) c) measurement of the resistance of the main circuit (Clause 7.3 of IEC60694); d) tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-102 | Witness & Report
29 | Type Tests | Certified Reports of test on the identical type according to IEC62271-102 or IEC129
DATA SHEET FOR CUT OUT FUSE (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Class | Outdoor
2 | Type | Channel Type
3 | Manufacturer of Fuse base & link | By Vendor
4 | Applicable Standard | IEC60282 , IEC60787, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
5 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
6 | Nominal line to line voltage rating (kV) | 11
7 | Maximum continuous line to line operating voltage (kV) | 12
8 | Rated frequency (Hz) | 50
9 | Color of Porcelain insulator | By Vendor
10 | Rated current of Fuse base (A) | 100
11 | Rated current of Fuse link (A) | 10
12 | Creepage distance (mm/kV) | 31
13 | Minimum creepage distance of insulator (mm) | 372
14 | Rated maximum braking current (kA) | 16
15 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
16 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
17 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
18 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
19 | Fuse class | Full-range
20 | Operating pole | Required
21 | Mounting brackets and accessories | Required
22 | Provision for mounting of surge arrester | Required
23 | Weight of Fuse-base & Fuse link | By Vendor
24 | Dimension of Fuse-base | By Vendor
25 | Dimension of Fuse-link | By Vendor
26 | Pollution condition | Heavy
27 | Minimum data required on rating plate | On the fuse base: Manufacturer's name Manufacturer's type designation Rated insulation level Rated voltage Rated current On the fuse carrier: Manufacturer's name Rated voltage Rated current Rated breaking capacity and TRV class Rated frequency On the fuse links: Manufacturer's name Manufacturer's type designation Rated current and speed designation Rated voltage
28 | Routine Tests | Witness and Report according to IEC 60282-2
29 | Type Tests | Certified Report on the identical type according to IEC 60282-2
DATA SHEET FOR LIGHTNING ARRESTER (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | ZnO
2 | Applicable Standard | IEC60099-4, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal line to line voltage rating (kV) | 11
5 | Maximum continuous line to line operating voltage (kV) | 12
6 | Continuous Operating Voltage (Ucov) | 9.6
7 | Rated frequency (Hz) | 50
8 | Material of insulator | By vendor
9 | Earth fault factor | 1.4
10 | Line discharge class per IEC 60099-4 | 2
11 | Minimum energy discharge capability (kJ/kV) U rated | Acc. To IEC
12 | Nominal discharge current with 8/20 microsecond wave (kA peak) | 10
13 | Pressure relief class (kA) | 20
14 | Creepage distance (mm/kV) | 31
15 | Minimum creepage distance of insulator (mm) | 372
16 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
17 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
18 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
19 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
20 | Whether surge counter required? | No
21 | Washable in service | Yes
22 | Temporary overvoltage factor (Ktov) at 1 Sec. at 10 Sec. at 100 Sec. | By vendor
23 | 5kA, 8/20µs lightning impulse protective level | By vendor
24 | 10kA, 8/20µs lightning impulse protective level (Ur 10kA, 8/20) | Residual voltage < 43.2kV
25 | 20kA, 8/20µs lightning impulse protective level | By vendor
26 | 125A, 30/60µs switching impulse protective level | By vendor
27 | Height of Surge Arrester | By vendor
28 | Diameter of Sheds | By vendor
29 | Total Weight of Surge Arrester | By vendor
30 | Type and Material of Terminal | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Manufacturer type designation Serial number Continuous operating voltage Rated voltage Rated frequency Nominal discharge current Pressure relief short time current Line discharge current Pollution degree Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Measurement of reference voltage Uref (Clause 8.1.a of IEC 60099-4) b) Residual voltage test (Clause 8.1.b of IEC 60099-4) c) Internal Partial Discharge test (Clause 8.1.c of IEC 60099-4); d) Leakage test for sealed housing arresters (Clause 8.1.d of IEC 60099-4) e) Design and visual checks acc. to purchase specifications | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 60099-4
DATA SHEET FOR LOAD BREAK SWITCH (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IEC 62271-103, IEC 60694, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type | SF6
5 | Rated Voltage | 11kV
6 | Rated Frequency | 50Hz
7 | No. of Phases and Poles | 3 Phase, 3 Pole
8 | 1 minute power freq. withstand voltage To earth and between phases: Across isolating distance: | 28kV 32kV
9 | Lightning impulse withstand voltage To earth and between phases: Across isolating distance: | 60kV 75kV
10 | Rated Normal Current | 630 A
11 | Mainly active load breaking current | By vendor (> 200A)
12 | Closed loop breaking current | By vendor
13 | Line charging breaking current | By vendor
14 | Cable charging breaking current | By vendor
15 | No load transformer breaking current | By vendor (> 0.74A)
16 | Rated Short Time Withstand Current | 25kA, 3 Sec.
17 | Rated Peak Withstand Current | 62.5kA
18 | Rated Short Circuit Making Current | 62.5kA
19 | Number of breaking operation CO | By vendor
20 | Supporting Structure Material | Hot dipped galvanized steel
21 | Creepage distance (mm/kV) | 31
22 | Min. Creepage Distance of insulators | 372mm
23 | Ingress protection of el. Enclosures | Min. IP55
24 | Operating mechanism | Hand operated mechanism, common for three poles
25 | Permissible tensile force on terminals | By vendor
26 | Gas pressure indicator | Required
27 | Auxiliary Contacts: No. of Make Contacts No. of Break Contacts Rated Voltage Rated Current Breaking Current at 110V DC | By vendor: Min. 4 Min. 4 110V DC Min. 10A Min. 2A
28 | Anti-Condensation Heater | 230V AC, 1Ph, 50Hz
29 | Interlocks with Earth Switch | Load Break Switch + Earth Switch integrated as one unit
30 | Dimensions and Weight | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Type designation and serial number Rated voltage One minute power frequency withstand voltage Lightning impulse withstand voltage Rated normal current Rated short time withstand current Mainly active load breaking current Closed loop breaking current Line charging breaking current Cable charging breaking current No load transformer breaking current Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Dielectric test on the main circuit (Clause 7.1 of IEC 60694) b) Tests on auxiliary and control circuits (Clause 7.2 of IEC 60694) c) Measurement of the resistance of the main circuit (Clause 7.3 of IEC60694) d) Tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-100 | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 62271-103
DATA SHEET FOR TOWER (W007S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 440
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type of Steel: Analysis of steel Carbon Manganese Sulphur Phosphorus Silicon | MILD High Strength ST 37(235JR) ST 52(355JR) 0.17 0.2 1.4 1.6 0.045 0.05 0.045 0.05 0.3 0.55
5 | Thickness of steel (1.6-3.2mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 65 65 460
6 | Thickness of steel (3.2-4.8mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 75 75 530
7 | Thickness of steel (4.8-6.4mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 85 85 600
8 | Strength in Tension Standard Designation | BS 8100 – Lattice Towers and Masts
9 | Strength in Tension (Ultimate tensile stress) | 340-470 490-630
10 | Strength in Tension (Yield stress) | 235 355
11 | Strength in Compression (Elongation) | 24% 22%
12 | Strength in Compression (Min zinc coating) | 85μ 85μ
13 | Bolts & Nuts Characteristics: Standard designation Steel material Property class Ultimate shearing stress (On bolt shank) Ultimate Bearing stress Min zinc coating | ANSI C 135-1 (Galvanized Steel Bolts and Nuts for Overhead Lines) Steel Steel 5.6 5.8 2100kg/cm2 2800kg/cm2 5400kg/cm2 6000kg/cm2 46μ 46μ
14 | Pollution condition | Heavy
15 | Routine tests & Type test | According to ASCE1090 Manual 52
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 33 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 34 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 35 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 36 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 37 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 38 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 39 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 40 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 41 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 42 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK

## W046S
DATA SHEET FOR PHASE CONDUCTOR (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Conductor Name | HYENA
5 | Applicable standard | ASTM B232, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
6 | Max allowable temperature of conductor (°c) | 85
7 | Reted short circuit current for 0.5 Sec. (KA) | 18.8
8 | Max. temperature range (operation) | 75
9 | Temperature range for installation(°c) | -5 ~ +55
10 | Stranding and wire diameter (nos./mm):
11 | Aluminium | 7/4.39
12 | Steel | 7/1.93
13 | Overall diameter(mm) | 14.57
14 | Aluminium Area (mm²) | 106
15 | Steel area (mm²) | 20.48
16 | Total area (mm²) | 126.2
17 | Weight (kg/km):
18 | Aluminium | 290
19 | Steel | 160
20 | Total | 450
21 | Nominal current in 30° (A) | 441
22 | Ultimate tensile Strength (kg) | 4090
23 | Coefficient of linear expansion (1 /C° x 10-6) | 18.8
24 | Initial modulus of elasticity (kg/mm²) | 6000
25 | Final modulus of elasticity (kg/mm²) | 7450
26 | DC resistance at 20°C(Ω/km) | 0.2713
27 | AC resistance at 25°C(Ω/km) | 0.277
28 | AC resistance at 75°C(Ω/km) | 0.3142
29 | Temperature range (transport / storage) | By vendor
30 | Pollution condition | Heavy
31 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR SHIELD WIRE (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacture | By vendor
2 | Year of Manufacture | By vendor
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Code Name | 7No.8 AWG
5 | Applicable standard | ASTM B416, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 427
8 | Stranding and wire diameter (nos./mm): | 7/3.26
9 | Overall diameter(mm) | 9.78
10 | Total area (mm²) | 58.43
11 | Weight (kg/km): | 390
12 | Ultimate tensile Strength (kg) | 7226
13 | Coefficient of linear expansion (1 /C° x 10-6) | 13
14 | Initial modulus of elasticity (kg/mm²) | 16000
15 | Final modulus of elasticity (kg/mm²) | 16000
16 | DC resistance at 20°C(Ω/km) | 1.467
17 | Pollution condition | Heavy
18 | Routine tests & Type test | Acc To IEC 61089
DATA SHEET FOR INSULATOR (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | BALL & SOCKET
2 | Applicable Standard | IEC60120, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 426
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material | Porcelain
5 | Nominal line to line voltage rating (kV) | 11
6 | Maximum continuous line to line operating voltage (kV) | 12
7 | Rated frequency (Hz) | 50
8 | Creepage distance (mm/kV) | 31
9 | Minimum creepage distance of insulator (mm) | 372
10 | Minimum mechanical Failing Load (kN) | 70
11 | Socket coupling size (IEC60120) | 16
12 | Ball coupling size (IEC60120) | 16
13 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
14 | Rated lightning impulse withstand voltage across the isolating dist. of Fuse base (kVpeak) | 75
15 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
16 | Rated one minute PF withstand voltage across the isolating dist. of Fuse base (kVrms) | 32
17 | Power Frequency Puncture Voltage (kV) | 110
18 | Metallic Part material | Malleable Cast Iron
19 | Insulator material | Brown Glazed Porcelain
20 | Metallic parts | Malleable cast iron
21 | Washable in service | Yes
22 | Unit Spacing (mm) | By vendor
23 | Disc Diameter (mm) | By vendor
24 | Total Weight | By vendor
25 | Type and Material of Terminal | By vendor
26 | Pollution condition | Heavy
27 | Routine tests & Type test | Acc To IEC 383
DATA SHEET FOR FITTING SUSPENSION & TENSION SET (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | FORGED STEEL
2 | Applicable standard | IEC 61284, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 465
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Material: | -
5 | Outer Part | AL.ALLOY
6 | Iner Part | FORGED STEEL, Hot Deep Galvanized.
7 | Jumper Plate | AL.ALLOY
8 | Terminal Jumper | AL.ALLOY
9 | Bolts & Nuts & Washers | STEEL, Hot Deep Galvanized.
10 | Split Pin | STAINLESS STEEL
11 | Min breaking strength | 95% OF CONDUCTOR U.T.S
12 | Coupling Standard IEC | 16 mmA
13 | Short Circuit Current | 25kA/0.4Sec.
14 | Arcing Horn | STEEL
15 | Min breaking strength (KN) | 80
16 | Anti-Climbing Devices and Safety Signs for Lines up to 400kV | ENA TS 43-90
17 | Tower Identification | Steel Sheet with 2mm Thickness
18 | Danger Alarm | Steel Sheet with 1.2mm Thickness
19 | Pollution condition | Heavy
20 | Routine tests & Type test | Acc To IEC 61284
DATA SHEET FOR EARTHING SYSTEM (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | GROUND WIRE :
2 | Type | Copper Conductor
3 | Applicable standard | DIN 48201, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 409
4 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
5 | Stranding (No./mm) | 7/2.5
6 | Total cross section (mm2) | 35
7 | Overall Diameter (mm) | 7.5
8 | Unit Weight (kg/m) | 0.31
9 | Calculated breaking load (kN) | 13.77
10 | DC Resistance At 20°C (ohm/km) | 0.5265
11 | TOWER BONDING CLAMP :
12 | Type of Body | Forged Steel
13 | Surface Coating | HOT DIP. GALV. Acc to ASTM A123 & A153 or BS729
14 | Type of Bolt & Nut | Steel
15 | Torgue on Bolt | 20 NM
16 | Applicable standard | ST37 & DIN931,934,125,127
17 | Diameter of Wire catcher | Ø 8-13 mm
18 | Pollution condition | Heavy
19 | Routine tests & Type test | Acc To DIN 48201
DATA SHEET FOR DISCONNECTOR SWITCH (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Installation (indoor / outdoor) | Outdoor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal system voltage, 3phase | 11 kV
5 | System voltage variation | ± 10%
6 | Nominal frequency and frequency variation | 50 ± 5%
7 | Numbers of poles and current rating | 3pole / 630 A
8 | Short circuit amper and time duration | 25 kA / 1 s
9 | Rated peak withstand current | 62.5 kA
10 | Creepage distance (mm/kV) | 31
11 | Minimum creepage distance of insulator (mm) | 372
12 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
13 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
14 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
15 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
16 | Mode of operation OPEN/CLOSE | open-close manual and with earth blad and earth switch manual
17 | Disconnectors & Earthing switches Operating | Hand operating
18 | Accessories | with earth blad and earth switch manual
19 | Disconnector Mechanism | Center break
20 | Construction | Three pole operation Containing Earthing switch
21 | Ingress protection of electrical enclosures | Min. IP55 (If Needed)
22 | Disconnector status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
23 | Earthing switch status Auxiliary Contacts: No. Of Make Contacts No. Of Break Contacts Rated Voltage Rated Current Breaking Current At 110V DC | 12NC (Normally close) 12NO (Normally open) 110V DC 25 ADC 5 ADC
24 | Interlocks(Electrical & Mechanical) | To prevent closure of earth switch when Disconnector is not in open position To prevent closure of Disconnector when earth switch is not in open position
25 | Dimensions & weights | By Vendor
26 | Pollution condition | Heavy
27 | Minimum Rating plate data | Manufacturer Type designation and serial number Rated voltage Rated lightning impulse withstand voltage across open pole Rated lightning impulse withstand voltage between poles Rated power frequency withstand voltage across open pole Rated power frequency withstand voltage between poles Rated normal current Rated duration of short circuit Rated no load transformer breaking current Year of manufacture Relevant standard with date of issue
28 | Routine Tests: a) dielectric test on the main circuit (clause 7.1 of IEC60694) b) tests on auxiliary and control circuits (Clause 7.2 of IEC60694) c) measurement of the resistance of the main circuit (Clause 7.3 of IEC60694); d) tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-102 | Witness & Report
29 | Type Tests | Certified Reports of test on the identical type according to IEC62271-102 or IEC129
DATA SHEET FOR CUT OUT FUSE (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Class | Outdoor
2 | Type | Channel Type
3 | Manufacturer of Fuse base & link | By Vendor
4 | Applicable Standard | IEC60282 , IEC60787, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
5 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
6 | Nominal line to line voltage rating (kV) | 11
7 | Maximum continuous line to line operating voltage (kV) | 12
8 | Rated frequency (Hz) | 50
9 | Color of Porcelain insulator | By Vendor
10 | Rated current of Fuse base (A) | 100
11 | Rated current of Fuse link (A) | 10
12 | Creepage distance (mm/kV) | 31
13 | Minimum creepage distance of insulator (mm) | 372
14 | Rated maximum braking current (kA) | 16
15 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
16 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
17 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
18 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
19 | Fuse class | Full-range
20 | Operating pole | Required
21 | Mounting brackets and accessories | Required
22 | Provision for mounting of surge arrester | Required
23 | Weight of Fuse-base & Fuse link | By Vendor
24 | Dimension of Fuse-base | By Vendor
25 | Dimension of Fuse-link | By Vendor
26 | Pollution condition | Heavy
27 | Minimum data required on rating plate | On the fuse base: Manufacturer's name Manufacturer's type designation Rated insulation level Rated voltage Rated current On the fuse carrier: Manufacturer's name Rated voltage Rated current Rated breaking capacity and TRV class Rated frequency On the fuse links: Manufacturer's name Manufacturer's type designation Rated current and speed designation Rated voltage
28 | Routine Tests | Witness and Report according to IEC 60282-2
29 | Type Tests | Certified Report on the identical type according to IEC 60282-2
DATA SHEET FOR LIGHTNING ARRESTER (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Type | ZnO
2 | Applicable Standard | IEC60099-4, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Nominal line to line voltage rating (kV) | 11
5 | Maximum continuous line to line operating voltage (kV) | 12
6 | Continuous Operating Voltage (Ucov) | 9.6
7 | Rated frequency (Hz) | 50
8 | Material of insulator | By vendor
9 | Earth fault factor | 1.4
10 | Line discharge class per IEC 60099-4 | 2
11 | Minimum energy discharge capability (kJ/kV) U rated | Acc. To IEC
12 | Nominal discharge current with 8/20 microsecond wave (kA peak) | 10
13 | Pressure relief class (kA) | 20
14 | Creepage distance (mm/kV) | 31
15 | Minimum creepage distance of insulator (mm) | 372
16 | Rated lightning impulse withstand voltage to earth and between poles (kV peak) | 60
17 | Rated lightning impulse withstand voltage across the isolating distance of Fuse - base(kV peak) | 75
18 | Rated one minute power frequency withstand voltage to earth and between poles (kV rms) | 28
19 | Rated one minute power frequency withstand voltage across the isolating distance of Fuse - base (kV rms) | 32
20 | Whether surge counter required? | No
21 | Washable in service | Yes
22 | Temporary overvoltage factor (Ktov) at 1 Sec. at 10 Sec. at 100 Sec. | By vendor
23 | 5kA, 8/20µs lightning impulse protective level | By vendor
24 | 10kA, 8/20µs lightning impulse protective level (Ur 10kA, 8/20) | Residual voltage < 43.2kV
25 | 20kA, 8/20µs lightning impulse protective level | By vendor
26 | 125A, 30/60µs switching impulse protective level | By vendor
27 | Height of Surge Arrester | By vendor
28 | Diameter of Sheds | By vendor
29 | Total Weight of Surge Arrester | By vendor
30 | Type and Material of Terminal | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Manufacturer type designation Serial number Continuous operating voltage Rated voltage Rated frequency Nominal discharge current Pressure relief short time current Line discharge current Pollution degree Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Measurement of reference voltage Uref (Clause 8.1.a of IEC 60099-4) b) Residual voltage test (Clause 8.1.b of IEC 60099-4) c) Internal Partial Discharge test (Clause 8.1.c of IEC 60099-4); d) Leakage test for sealed housing arresters (Clause 8.1.d of IEC 60099-4) e) Design and visual checks acc. to purchase specifications | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 60099-4
DATA SHEET FOR LOAD BREAK SWITCH (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IEC 62271-103, IEC 60694, IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type | SF6
5 | Rated Voltage | 11kV
6 | Rated Frequency | 50Hz
7 | No. of Phases and Poles | 3 Phase, 3 Pole
8 | 1 minute power freq. withstand voltage To earth and between phases: Across isolating distance: | 28kV 32kV
9 | Lightning impulse withstand voltage To earth and between phases: Across isolating distance: | 60kV 75kV
10 | Rated Normal Current | 630 A
11 | Mainly active load breaking current | By vendor (> 200A)
12 | Closed loop breaking current | By vendor
13 | Line charging breaking current | By vendor
14 | Cable charging breaking current | By vendor
15 | No load transformer breaking current | By vendor (> 0.74A)
16 | Rated Short Time Withstand Current | 25kA, 3 Sec.
17 | Rated Peak Withstand Current | 62.5kA
18 | Rated Short Circuit Making Current | 62.5kA
19 | Number of breaking operation CO | By vendor
20 | Supporting Structure Material | Hot dipped galvanized steel
21 | Creepage distance (mm/kV) | 31
22 | Min. Creepage Distance of insulators | 372mm
23 | Ingress protection of el. Enclosures | Min. IP55
24 | Operating mechanism | Hand operated mechanism, common for three poles
25 | Permissible tensile force on terminals | By vendor
26 | Gas pressure indicator | Required
27 | Auxiliary Contacts: No. of Make Contacts No. of Break Contacts Rated Voltage Rated Current Breaking Current at 110V DC | By vendor: Min. 4 Min. 4 110V DC Min. 10A Min. 2A
28 | Anti-Condensation Heater | 230V AC, 1Ph, 50Hz
29 | Interlocks with Earth Switch | Load Break Switch + Earth Switch integrated as one unit
30 | Dimensions and Weight | By vendor
31 | Pollution condition | Heavy
32 | Minimum data required on rating plate | Manufacturer Type designation and serial number Rated voltage One minute power frequency withstand voltage Lightning impulse withstand voltage Rated normal current Rated short time withstand current Mainly active load breaking current Closed loop breaking current Line charging breaking current Cable charging breaking current No load transformer breaking current Year of manufacture Relevant standard with date of issue
33 | Routine Tests a) Dielectric test on the main circuit (Clause 7.1 of IEC 60694) b) Tests on auxiliary and control circuits (Clause 7.2 of IEC 60694) c) Measurement of the resistance of the main circuit (Clause 7.3 of IEC60694) d) Tightness test (Clause 7.4 of IEC60694) e) Design and visual checks (Clause 7.5 of IEC60694) f) Mechanical tests as per clause 7.101 of IEC62271-100 | Witness and Report
34 | Type Tests | Certified Report on the identical type according to IEC 62271-103
DATA SHEET FOR TOWER (W046S)
Item | DESCRIPTION | CHARACTERISTIC | Vendor data
1 | Manufacturer / Country | By vendor
2 | Standard | IPS-E-EL-160, Islamic Republic of Iran Vice Presidency for Strategic Planning and Supervision, General Technical Specification and Execution Procedures for overhead and cable power distribution lines NO: 374,375 & General Technical Specification and Execution Procedures for Transmission Lines NO: 440
3 | Environmental conditions | Acc. to document number: BK-00-HD-000-PR-DB-0001 (Process Basis of Design)
4 | Type of Steel: Analysis of steel Carbon Manganese Sulphur Phosphorus Silicon | MILD High Strength ST 37(235JR) ST 52(355JR) 0.17 0.2 1.4 1.6 0.045 0.05 0.045 0.05 0.3 0.55
5 | Thickness of steel (1.6-3.2mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 65 65 460
6 | Thickness of steel (3.2-4.8mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 75 75 530
7 | Thickness of steel (4.8-6.4mm): Galvanizingdegree Coating thickness (μm) Coating thickness* gr/m² * Thickness amounts in μm are the galvanizing degree. this are calculated from gr/m2=μm*7.067 | 85 85 600
8 | Strength in Tension Standard Designation | BS 8100 – Lattice Towers and Masts
9 | Strength in Tension (Ultimate tensile stress) | 340-470 490-630
10 | Strength in Tension (Yield stress) | 235 355
11 | Strength in Compression (Elongation) | 24% 22%
12 | Strength in Compression (Min zinc coating) | 85μ 85μ
13 | Bolts & Nuts Characteristics: Standard designation Steel material Property class Ultimate shearing stress (On bolt shank) Ultimate Bearing stress Min zinc coating | ANSI C 135-1 (Galvanized Steel Bolts and Nuts for Overhead Lines) Steel Steel 5.6 5.8 2100kg/cm2 2800kg/cm2 5400kg/cm2 6000kg/cm2 46μ 46μ
14 | Pollution condition | Heavy
15 | Routine tests & Type test | According to ASCE1090 Manual 52
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 43 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 44 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 45 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 46 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 47 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 48 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 49 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 50 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 51 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK
تسهیلات
Data Sheets For 11 KV Over Head Line Equipment
شماره صفحه: 52 از 52
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیتهای رو زمینی در بستههای کاری تحتالارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
DT
0012
D04
بسته کاری
SSGRL
پروژه
BK