## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0004_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0939 |  |  | Transmital Date: 14-May-2022
Document Title: Calculation Note For Lighting System of Well Pads Area |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0939 |  |  | Transmital Date: 14-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-CN-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on Plot Plan Drawing and hazardous area classification layout documents. |  | BK-SUR-ENG-ELE-01-04389 | 2022-05-23 | در صورت هر گونه تغییر در مدارک مطرح شده این مدرک ویرایش خواهد شد.
2 | According to our telephone conversation following items shall be added or modified: |  | BK-SUR-ENG-ELE-01-04389 | 2022-05-23
2-1 | A separat table shall be added to this document and shall be compared calculated Lux with IPS-E-EL-100 standard to check the result of calculation. |  | BK-SUR-ENG-ELE-01-04389 | 2022-05-23 | نوت مربوط به مقایسه محاسبات و مقدار لوکس مورد نیاز استاندارد در این محوطه اضافه گردید.
2-2 | Dimension of buildings and shelters shall be modified and outdoor lighting fixturers around the building shall be added in lighting calculation to considered impact of these lighting fixturers in calculation. |  | BK-SUR-ENG-ELE-01-04389 | 2022-05-23 | مطابق با مذاکرات انجام شده مقرر گردید، جهت جلوگیری از ایجاد خطا و همچنین کم کردن میانگین روشنایی، ساختمانها در محاسبات حذف شوند. ولی در انتها، نقشه پلات به صورت کامل با حضور ساختمانها نشان داده شده است.
3 | Complementary comments will be submitted after received revised documents. |  | BK-SUR-ENG-ELE-01-04389 | 2022-05-23 | موارد در نظر گرفته خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 23-May-22 |  |  |  |  | Date: