## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | IN | DT | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | JUL.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707369
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | IN | DT | 0002 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 8
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0002 | D02
REFERENCE DOCUMENTS:
1- SPECIFICATION FOR INSTRUMENTATION | [9 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
2-PIPELINE MATERIAL SPECIFICATION | [9 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
3- PIPING & INSTRUMENT DIAGRAM:
| P&ID - W018S | [8 empty] | BK-W018S-PEDCO-110-PR-PI-0001
| P&ID - W028 | [8 empty] | BK-W028-PEDCO-110-PR-PI-0001
| P&ID - W035 | [8 empty] | BK-W035-PEDCO-110-PR-PI-0001
| P&ID - W008N | [8 empty] | BK-W008N-PEDCO-110-PR-PI-0001
| P&ID - W007S | [8 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| P&ID - W046S | [8 empty] | BK-W046S-PEDCO-110-PR-PI-0001
4-PROCESS FLOW DIAGRAM (PFD) | [9 empty] | BK-GCS-PEDCO-120-PR-PF-0001
5-INSTRUMENT & CONTROL SYSTEM DESIGN CRITERIA | [9 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
6- SPECIFICATION FOR WHCP/HPU | [9 empty] | BK-SSGRL-PEDCO-110-IN-SP-0001

## Note
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0002 | D02
GENERAL NOTES:
1- Pressure elements shall be capable of withstanding intermittent over-ranging to 1.3 times the maximum scale reading.
2- Ranges shall be selected suitable to have the operating pressure in the middle third of the scale.
3- Vendor is responsible for applying suitable accessories to prevent damage and to reach required accuracy for PI.
4- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
5- All field instruments shall be furnished with a stainless steel corrosion resistant nameplate permanently fastened with screws and stamped as follows and as applicable:
· Vendor’s name
· Model number
· Serial number
· Instrument tag number
· Operating range
· hazardous area certification & certification agency name
· Pressure rating
6- Weep hole shall be provided on the case bottom of all gauges.
7- Material Test Certificate and Calibration Certificate for all gauges to be submitted by vendor.
8- Each pressure gauge which doesn’t have Diaphragm Seal shall be supplied with a Two valve manifold (block & bleed manifold) ( Process Conn. 1/2"NPTF, 316 S.S.). Manifold to be supplied by vendor
.
9- Environmental Condition For Field Instrumentation Of BINAK Oil field Shall Be Considered As Per The Following:
• Minimum ambient temperature (°C): -5 °C • Maximum ambient temperature (°C): 50 °C • Maximum steel surface exposed to sun (°C): 85 °C • Maximum Design relative humidity: 100% • Minimum Design relative humidity: 0%

## PG
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  |  | BK | SSGRL | PEDCO | 000 |  | IN | DT | 0002 |  | D02
Pressure Gauge
GENERAL | 1 | Item | [6 empty] | See List
| 2 | Tag Number | [6 empty] | See List
| 3 | Service | [6 empty] | See List
| 4 | Line Number /Equipment | [6 empty] | See List
| 5 | P&ID No. | [6 empty] | See List | [5 empty] | See List
PROCESS CONDITIONS | 6 | Fluid |  | Fluid State |  |  |  |  | See List | [5 empty] | See List
| 7 | Oper. Pressure |  | Design Pressure (barg) |  |  |  |  | See List |  |  |  | bar-g |  | See List | bar-g
| 8 | Oper. Temp. |  | Design Temp. (°C) |  |  |  |  | See List | [5 empty] | See List | °C | ؛C
MANIFOLD | 9 | Manifold Type |  | Manifold Material |  |  |  |  | 2-valve (block & bleed manifold) (Note 6) | [5 empty] | S.S 316
| 10 | Connection |  | Manifold Rating |  |  |  |  | 1/2" NPTF(note 2) | [5 empty] | Note 7
CASE | 11 | Case Type |  | Case Style |  |  |  |  | Filled type (with silicon oil) (note 4) | [5 empty] | vapour tight and weather proof (IP 65)
| 12 | Case Material |  | Case Size |  |  |  |  | stainless steel 304 | [5 empty] | 150 mm
| 13 | Case Pressure Relief | [6 empty] | Yes
| 14 | Conn. Location |  | Proc. Connection/ Rating |  |  |  |  | Direct Mounted from Bottom | [5 empty] | 1/2" NPTM/ See List
| 15 | Ring Style |  | Ring Material |  |  |  |  | VTA | [5 empty] | 316 S.S.
| 16 | Mounting Type |  | Blow-out protection |  |  |  |  | Local | [5 empty] | Back
| 17 | Socket Material | [6 empty] | 316 S.S.
| 18 | Window Material | [6 empty] | Shatterproof glass
| 19 | Seal / O-Ring Material | [6 empty] | VTA
ELEMENT | 20 | Liquid Fill Material | [6 empty] | VTA
| 21 | Element Type |  | Element Material |  |  |  |  | Bourdon (note 3, 8) | [5 empty] | 316 S.S.( note 1)
| 22 | Movement Style |  | Movement Material |  |  |  |  | VTA | [5 empty] | 316 S.S.
| 23 | Over Range Protection | [6 empty] | 1.3 times of maximum operating pressure
| 24 | Accuracy | [6 empty] | ±0.6 % of F.S.
| 25 | Internal Stop | [6 empty] | Yes
| 26 | Measuring Range | [6 empty] | See List | [5 empty] | bar-g
DIAL | 27 | Dial Scale Type |  | Dial Material |  |  |  |  | Dual indicating scales (barg/psig) | [5 empty] | aluminum
| 28 | Dial Color | [6 empty] | Black marks on white background
| 29 | Zero Adjustment | [6 empty] | Adjustable pointer (note 5)
ACCESSORY | 30 | Syphon |  | Material |  |  |  |  | See List | [5 empty] | 316 S.S. (Note 1)
| 31 | Pulsation Damper |  | Material |  |  |  |  | See List ,see 'P.D.' tab column | [5 empty] | 316 S.S. (Note 1)
| 32 | Over Press. Protector |  | Material |  |  |  |  | See List | [5 empty] | VTA
| 33 | End Connection | [6 empty] | 1/2" NPT(note 2)
DIAPHRAGM SEAL (Note 9) | 34 | Seal Type | [6 empty] | N/A
| 35 | Instrument Conn. |  | Process Conn. |  |  |  |  | N/A | [5 empty] | N/A
| 36 | Diaphragm Extension Length | [6 empty] | N/A
| 37 | Diaphragm Material | [6 empty] | N/A
| 38 | Capillary Material |  | Capillary Length |  |  |  |  | N/A | [5 empty] | N/A
| 39 | Housing Mtrl. | Upper | Lower |  |  |  |  | N/A | [5 empty] | N/A
| 40 | Bolting Material | [6 empty] | N/A
| 41 | Gasket / O-Ring Material | [6 empty] | N/A
| 42 | Fill Fluid Material | [6 empty] | N/A
SPECIAL | 43 | Note |  | NACE MR0175/ISO 15156 Compliance |  |  |  |  | See List | [5 empty] | See List(Note 1)
PURCHASE | 44 | Manufacturer | [6 empty] | WILL BE FINALIZED LATER
| 45 | Model | [6 empty] | WILL BE FINALIZED LATER
Notes:
VTA : Vendor to Advise
N/A: Not Applicable
1 : Wetted part shall be according To MR0175/ISO 15156 as per table page 6.
2: 1/2"NPT for Instrument/Process connection and 1/4" NPTF for Drain Connection-All Manifolds ,Pulsation Dampners and Syphons shall be suitable for connecting to gauges.
3: Suitable element type for gauge to be confirmed by vendor .
4: Cases for pressure gauges shall be solid front stainless steel.
5: Gauge pointer shall be adjustable (micro meter adjustment) without removal from pinion shaft.
6: Valves manifold with mounting bracket, u-bolts and nuts shall be supplied by vendor.
7: For manifoled rating, Bolt & Gasket material refer to "Piping and Pipeline Material Specification No.: BK-SSGRL-PEDCO-110-PL-SP-0001"
8: Over-range stopper shall be provided for the over-range limit.
D02
D02
D02

## LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR PRESSURE GAUGE - WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO | 000 | IN | DT | 0002 | D02
Item | Tag No. | Service | P&ID |  |  | Equipment/ Line No. |  | Fluid | State | Pressure Measuring Range (barg) | Press. Oper. (barg) | Press. Des. (barg) | Oper. Tem. (°C) | Design Tem. (°C) | Diaphragm Seal Requirement | NACE | Syphon | P.D. | Over Range Protection (NOTE 1) | Conn. Rating | Remark | REVISION
1 | PG-1201 | W007S | BK-W007S-PEDCO-110-PR-PI-0002 |  |  | CRD-110-120-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 80 | 105 | NO | Yes | NO | NO | YES | 3000#
2 | PG-1202 | W007S | BK-W007S-PEDCO-110-PR-PI-0002 |  |  | CRD-110-121-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-40 (Note 1) | 16.38 | 205.8 | 80 | 105 | NO | Yes | NO | NO | YES | 3000#
3 | PG-1601 | W008N | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | CRD-110-160-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 75 | 105 | NO | Yes | NO | NO | YES | 3000#
4 | PG-1602 | W008N | BK-W008N-PEDCO-110-PR-PI-0001 |  |  | CRD-110-161-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-25 (Note 1) | 12 | 205.8 | 74.02 | 105 | NO | Yes | NO | NO | YES | 3000#
5 | PG-1101 | W018S | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | CRD-110-110-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 75 | 105 | NO | Yes | NO | NO | YES | 3000#
6 | PG-1102 | W018S | BK-W018S-PEDCO-110-PR-PI-0001 |  |  | CRD-110-111-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-40 (Note 1) | 15.60 | 205.8 | 74 | 105 | NO | Yes | NO | NO | YES | 3000#
7 | PG-1401 | W028 | BK-W028-PEDCO-110-PR-PI-0001 |  |  | CRD-110-140-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 80 | 105 | NO | Yes | NO | NO | YES | 3000#
8 | PG-1402 | W028 | BK-W028-PEDCO-110-PR-PI-0001 |  |  | CRD-110-141-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-40 (Note 1) | 20.44 | 205.8 | 79.93 | 105 | NO | Yes | NO | NO | YES | 3000#
9 | PG-1501 | W035 | BK-W035-PEDCO-110-PR-PI-0001 |  |  | CRD-110-150-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 80 | 105 | NO | Yes | NO | NO | YES | 3000#
10 | PG-1502 | W035 | BK-W035-PEDCO-110-PR-PI-0001 |  |  | CRD-110-151-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-40 (Note 1) | 22.48 | 205.8 | 79.85 | 105 | NO | Yes | NO | NO | YES | 3000#
11 | PG-1301 | W046S | BK-W046S-PEDCO-110-PR-PI-0001 |  |  | CRD-110-130-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-100 (Note 1) | 43.8 | 205.8 | 80 | 105 | NO | Yes | NO | NO | YES | 3000#
12 | PG-1302 | W046S | BK-W046S-PEDCO-110-PR-PI-0001 |  |  | CRD-110-131-LN15-6"-PT |  | HC+WATER | LIQUID/GAS | 0-40 (Note 1) | 20.88 | 205.8 | 79.15 | 105 | NO | Yes | NO | NO | YES | 3000#
NOTES: 1- For this PG design pressure is more than 1.3 times the maximum scale reading so Pressure valve protector shall be used .
D02