## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-IN-DT-0002_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0660 |  |  | Transmital Date: 2 Mar 2022
Document Title: Data Sheets For Pressure Gauge - Wellheads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-IN-TR-0660 |  |  | Transmital Date: 2 Mar 2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-IN-DT-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | بازگشت به كامنت شماره 3، تاييد كارفرما اخذ گردد. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | انجام شد.
2 | موارد مربوط به PURCHASE به Will be finalized later تغيير پيدا كند. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | انجام شد.
3 | بازگشت به كامنت شماره 5، مدرك قبلي، Accuracy اصلاح شود. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | مطابق آخرین نامه کارفرما ، Accuracy اصلاح شد.
4 | Dual scale در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | مطابق آیتم 27 در نظر گرفته شده است.
5 | تاييد بخش فرآيند براي رنج ها گرفته شود. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | انجام شد.
6 | فشار هاي عملياتي بر اساس آخرين مدرك PFD نهايي شود. براي مثال PG-1602 |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | انجام شد.
Process Comments
7 | كامنت پيشين: پاسخ پيمانكار قانع كننده نبود و لازم است بدليل مشخصات فرايندي و عملكردي رنج فشارسنج هاي بالادست چوك فلنج (براي PG-1201, 1601 موارد مشابه) 0-160 بار نسبي در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | رنج دستگاه مطابق استاندارد میبایست به طریقی انتخاب شود که فشار Operation در یک سوم میانی آن قرار بگیرد. برای محافظت در برابر فشار طراحی شیر Over range protection دیده شده است.
8 | عبارت MIX در قسمت Fluid مي بايست به HC +Water تغيير يابد. |  | BK-SUR-ENG-INS-00-03646 | 2022-03-16 | انجام شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 14 Mar 2022 |  |  |  |  | Date: