## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-IN-SP-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0234 |  |  | Transmital Date: 02 Feb 2022
Document Title: SPECIFICATION FOR INSTRUMENTATION |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0008-IN-TR-0234 |  |  | Transmital Date: 02 Feb 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-000-IN-SP-0001_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion | Client Conclusion
1 | "Each work packages of the Project" shall be specified clearly. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | The document of Design Criteria has been produced for the purpose. A work package is a building block of the work breakdown structure that allows the project management to define the steps necessary for completion of the work. As such, a work package can be thought of as a sub-project, which, when combined with other work package units, form the completed project. However short Description has been added in scope section.
2 | Process and instrument connection for each instrument type shall be specified clearly as a table. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | The data will be specified in Datasheet of each device. Moreover, the data will be specified in Instrument Index as well. |  |  | بر اساس نقطه نظر قبلي اصلاح گرد. process connectionجهت ارجاع و استنادبايد در اين مدرك يا يكي از specديگر بصورت كامل مشخص گردد | اعمال گردید.
3 | Following abbreviation shall be added: - PDCS - TGS |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | As Power Distribution Control System ( PDCS ) and Tang Gauging System (TGS) are not part of the project,so in the revision have been removed. |  |  | closed | اعمال گردید.
4 | The format of this document shall be more organized and clear. One section for each instrument type to be considered and all details shall be specified in related section. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Regarding the content of the docuemnt, we categrized all instruments of the project in this way, please let us know what is your intended arrangement can improve the succession: ----------- General Features of Sensors------------------------ 6.0 FIELD SENSORS ----------- General Features of Switches------------------------ 7.0 LOCAL SWITCHES 7.1 PRESSURE SWITCHES 7.2 TEMPERATURE SWITCHES 7.3 LEVEL SWITCHES ----------- General Features of Transmitters------------------------ 8.0 TRANSMITTERS 8.1 HOUSING/ WETTED PART MATERIAL OF TRANSMITTERS 8.2 ACCURACY OF TRANSMITTERS 8.3 MANIFOLD 8.4 DIAPHRAGM SEAL AND CAPILLARY SEALS 8.5 SWITCHES 8.6 GLAND CONNECTION -----------------Flow ------------------- 9.0 FLOW INSTRUMENTS 9.1 ORIFICE PLATE 9.2 VENTURI 9.3 VORTEX 9.4 PITOT TUBE (ANNUBARS) 9.5 VARIABLE AREA FLOW METERS (ROTAMETER) 9.6 POSITIVE DISPLACEMENT METER 9.7 CORIOLIS 9.8 TURBINE FLOW METER 9.9 ULTRASONIC 9.10 MAGNETIC FLOW METER 9.11 THERMAL MASS FLOW METER --------------------Level --------------------------- 10.0 LEVEL INSTRUMENTS 10.1 DIFFERENTIAL PRESSURE LEVEL MEASUREMENT 10.2 DISPLACEMENT TYPE LEVEL MEASUREMENT 10.3 GUIDED WAVE RADAR LEVEL MEASUREMENT 10.4 LEVEL GAUGES -----------------Pressure -------------------- 11.0 PRESSURE INSTRUMENTS 11.1 DIFFERENTIAL PRESSURE TRANSMITTERS 11.2 PRESSURE TRANSMITTER 11.3 PRESSURE GAUGE -------------------Temperature --------------------------- 12.0 TEMPERATURE INSTRUMENTS 12.1 THERMOWELL 12.2 TEMPERATURE GAUGES 12.3 TEMPERATURE TRANSMITTERS -------------------Corrosion Devices --------------------------- 13.0 CORROSION COUPON AND PROBE 13.1 CORROSION COUPONS 13.2 CORROSION PROBES |  |  | بر اساس نقطه نظر قبلي اصلاح گرد.با توجه به عدم ارائه spec جداگانه براي تجهيزات ابزاردقيق، اطلاعات بيشتر، براي تجهيزات مورد استفاده در اين پرو‍ژه ارائه گردد.بعنوان مثال براي TT,TW با رسم شكل مقادير U length,lagging,..مشخص گردد. موارد استفاده Displacementبجاي DP level,side mounted , top mounted,... لازم به ذكر است specification بعنوان مدرك پايه ،منبع اطلاعات قابل استناد و ارجاع پروژه براي مدارك ديگر مانند ديتا شيت مي باشد.لذا كليه اطلاعات لازم در ديتا شيت را بر اساس ارجاع به اين مدرك بايستي كامل نمود. | در رفرنس این مدرک به شماره استاندارد مربوط به u-lenght یعنی (IPS-D-IN-101) اشاره شده است که در آنجا با رسم شکل مقادیر u-length آورده شده است که مجددا در این مدرک نمی آوریم اما مقادیر u-length مطابق با سایز خط در بند 12 این مدرک آورده شده است. موارد استفاده displacment از نوع topو side و همچنین dp level در بند 10 آورده شده است و مواردی در مورد dp level transmitter اضافه گردیده است.
5 | There are many discripancies between detail of document for example, element type for pressure gauge is considered both capsule and burdon tube. Contractor to issue the next revision of document more preciesly. And descripancies for all instrument types shall be managed. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | As you know there are diverse type of sensing for diverse type of condition. Specification is for the purpose that all technical specification of instruments to be mentioned for all various cases. The approach is followed in all projects. For example, maybe at first design a gauge according to the Burdon Type, but in next stage - in terms of applicability- we want to change it to another type. If we have not mentioned anything related to the new type, there will not be reference to comply. So the docuemnt designs for all various cases. |  |  | چند مورد بعنوان نمونه ذكر مي گردد: در صفحه 42 مقدار PG:270 عنوان شده در صورتيكه مقادير تا 1000 ديده شده است، با توجه به اطلاعات فرايندي موجود در سايت و اين پروژه يكسان سازي شود. براي TT محدوديت خط تا 4" ذكر گرديده ولي در جدول 3". براي displacer Levelاندازه تا 3048 ارائه شده است ، با توجه به محدوديتها تا اندازه 2000 بررسي شود(در صورتيكه ارتفاع وسل ها بالاست بررسي گردد).امكان استفاده از switch در اين پروژه بررسي گردد. | صفحه ای dial داری 360 درجه می باشد که در این پروژه 270 درجه برای ما مهم هست که عدد 1000 برای این درجه معنی ندارد. * محدودیت TT در جدول برای سایز 3" حذف گردید. * این اندازه 3048 برای displacer مطابق با ips-e-in-140 می باشد که در رفرنس این مدرک آورده شده است و مدرک specification باید بصورت general همه موارد را در نظر بگیرد. محدویت تا اندازه 2000 یرای انتخاب وندور می باشدکه در تصمیم گیری نوع ترنسمیتر روی مدرک P&ID در نظر گرفته خواهد شد. * در این پروژه فقط LEVEL SWITCH در نظر گرفته می شود که در قسمت 7 این مدرک ، note مربوط به این سوئیچ اورده شده است.
6 | Despite previous comments about deleting unnecessary sections. It seems there are sections wich are not applicable for project. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Please specify which part of the document is your concern. Also as you know the document is general, as mentioned in the item 5, some issue mentioned just for any other changes in progression of the design. |  |  | بر اساس نقطه نظر قبلي اصلاح گردد.موارد مرتبط با تجهيزات ابزار دقيقي اين پروژه تكميل و ارسال گردد. لازم به ذكر است در اين مقطع از پروژه ،اطلاعات پايه طراحي مانند نوع ابزاردقيق ها بايستي نهايي شده باشد، لذا لازم است در عوض ارائه اطلاعات تجهيزات اضافي،پيمانكار اطلاعات كاربردي مرتبط با تجهيزات مورد استفاده را با توضيحات كاملتر ارسال نمايد.در صورت تغيير نوع تجهيزات مدارك مرتبط بايستي اصلاح گردد. | اصطلاحات لازم انجام شده و موارد مورد نیاز اضافه شده است. با توجه به AFC شدن مدرک توسط کارفرما، امکان حذف بند‌های مدرک نمی‌باشد.
7 | Please clarify the application of Turbine and vortex flow transmitters for Binak Project? |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Regarding to the current design, nowhere is used. But as mentioned in the above items the document is fully general including diverse items in case of designing requirement. |  |  | بر اساس نقطه نظر قبلي اصلاح گرد. ارجاع به آيتم 6 | اصطلاحات لازم انجام شده است با توجه به AFC شدن مدرک توسط کارفرما، امکان حذف بند‌های مدرک نمی‌باشد.
8 | Solid front shall be considered for all gauges. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | In page 40, the issue had been already mentioned. |  |  | بر اساس نقطه نظر قبلي اصلاح گرد. براي تمام PGدر نظر گرفته شود. (قيد 20BAR برداشته شود) | اصلاح گردید.
9 | The color of background of gauges shall be specified clearly. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | In page 40, the issue had been already mentioned. However, we put a word of "face" to be more clear for you. |  |  | با توجه به انتخاب دو واحد(BAR,PSI) رنگ واحدها ذكر گردد | در اکثر این dual scale ، صفحه ای dial سفید رنگ می باشد ولی نوشته های آن صفحه ممکن هست رنگی باشد.
10 | Sec. 5.4 SIGNAL TRANSMISSION "Major subsystems (such as ESD, FGS, UCPs, PDCS, HVAC, TGS) shall be linked to the PCS/DCS via redundant serial link, generally with MODBUS RTU serial link." - specify that Monitoring signals shall be transmitted via serial link. command, shutdown , ... signals between subsystems and ESD shall be transmitted via hardwire. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | concidered in the document |  |  | closed
11 | Sec. 5.6 HAZARDOUS PROTECTION - Hazardous area classification shall be specified as a reference document for this section. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Hazardous Area Classification mentioned in 3.3. |  |  | با توجه به بند 5.6 لازم است مشخصات كامل Gas group, temperatureبصورت كامل بيان شود. | مشخصات کامل gas group و temperature در استاندارد IEC 60079آورده شده است به دلیل پرهیز از مطالب تکراری در این مدرک ، این استاندارد در رفرنس این مدرک آورده شده است.
12 | Doc number for all referred documents shall be added. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | This has been exactly regarded in the document. |  |  | closed
13 | AVL shall be followed for procurement of all instruments. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Certified in AVL will be mentioned and asked in MR and all docuemnts connected to that. |  |  | closed
14 | Piping material specification shall be followed for Materials exposed to the process fluid. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | It will be mentioned in Datasheets. |  |  | PMSبعنوان مدرك مرجع ذكر گردد. | اصلاح گردید.
15 | Please clarify "For parts exposed to process fluid when not specified otherwise" in sec. 6. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | According to your comment, we revised the section and rewrote text clearly. |  |  | closed
16 | hand held communicator shall be provided for each working package (if required) |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | In section 8 has been already mentioned. However, it will be mentioned as note in Datasheet as well. |  |  | تعداد با توجه به work packagesبايستي مشخص گردد. در صورت نهايي نشدن تعداد، عدد از مدرك حذف گردد. | دو عدد work package در این مدرک نهایی می باشد که یکی برای منیفولد و یکی برای gcs و pipeline می‌باشد.
17 | Please clarify the meaning of static pressure in document. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Static pressure is a term used in fluid dynamics to define the amount of pressure exerted by a fluid that is not moving. Static pressure is typically measured using a force divided by an area, or measured in length units when using a pressure head. Static pressure, when combined with dynamic pressure, can be used to determine the total pressure of a system, such as in a pipe or tank. Principally, Static pressure is a pressure that does not vary with time. To put it more simply, the Static pressure for DPT/DPG is difference of pressure between two legs. For PT/PG the pressure is the Pressure gauge (Pg); i.e. when measured relative to the atmospheric pressure, the static pressure is the same as the gauge pressure. However, it is possible to measure the static pressure with a vacuum as the reference, so that the value measured equals the absolute pressure. Since absolute non-variation is not possible, the static pressure is essentially defined as the pressure that varies with time by less than 1% of the pressure gauge’s index value per second. |  |  | بمنظور پرهيز از برداشتهاي مختلف،كلمه staticحذف گردد. | از آنجائیکه مدرک AFC شده است لطفا در این مدرک اگر کلمه ای static باعث برداشت اشتباه شده است صراحتا اعلام نمایید.
18 | Corrossion coupun and probe sections shall be specify with more detail. All items of datasheet like clock of installation and monitoring, …. shall be specified clearly. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | All detail data will be specified in datasheet. Specification is not the place of putting all detail data, because a part of data of theses devices is that of Proces, or that of piping, and that of instrument. Our datahseet is exactly based on the structure and all engaged disciplines will specify such detail in it. |  |  | ارجاع به آيتم 6 | در مورد monitoring و installation در بند های 13.1 و 13.2 آورده شده است اما clock اضافه گردید.
19 | Detail data for pig signaller (Indocator/ Transmitter) shall be provided. |  | BK-SUR-ENG-INS-00-02169 | 2021-12-01 | Same as the item 18. |  |  | ارجاع به آيتم 6 | از آنجائیکه pig signaler در بسته های خریدی خاصی از جمله pipeline وجود دارد بنابراین توضیحات بیشتر در مورد pig ها در مدرک design criteria وجود دارد که در رفرنس این مدرک می باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: 06 Feb 2022 |  |  |  |  | Date: