## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0030-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0815 |  |  | Transmital Date: 16/Apr/2022
Document Title: Mechanical Data Sheets For Fire Water Main Pumps - Diesel Engine Driven |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-ME-TR-0815 |  |  | Transmital Date: 16/Apr/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0030-D01 |  |  | CRS Status:
item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Fuel daily tank shall be sized for 8 hours and all instruments such as level transmitter with HH/LL Alam and etc. are in vendor's scope of supply, so note 1 is note related to fuel daily tank. |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | Noted, this comment will be added to notes of mechanical data sheet.
2 | when using the packing for sealing of pump, the max droplet shall be specified as per IPS.it is mandatory however, it has been mentioned in IPS. |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | Maximum leakage rate of packing will be specified by vendor.
3 | if you have considered the Arc valve, it is acceptable, Min flow shall be considered, keep the note and mentioned Arc valve are in vendor's scope of supply. |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | There is no need to consider ARC valve. Please specify your reference for this comment.
4 | diesel shall be tested at 110% rated speed in Mechanical running test, it shall be mentioned, it will be affected on diesel selection |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | Noted, will be added as note to mechanical data sheet
5 | Diesel speed shall be mentioned as less than 2300 rpm, and it is mandatory however it is generally will be followed |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | Noted, will be added as note to mechanical data sheet
6 | pressure sensing lines are in the vendor's scope, it shall be mentioned here in addition to MR. |  | BK-SUR-ENG-MEC-01-04138 | 2022-05-07 | Noted, will be added as note to mechanical data sheet
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.Naserizadeh |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: 5/7/2022 |  |  |  |  | Date: 07/30/2022