## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-BD-0001_D03 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-0765 |  |  | Transmital Date: 30 Mar 2022
Document Title: Control/ESD/F&G System Block Diagram Configuration |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0765 |  |  | Transmital Date: 30 Mar 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-BD-0001_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | درپاسخ به reply sheet نامه 385430، نظر خاصی مطرح نمی باشد. |  | 01/2294/55898 | 1401/02/20 | -
2 | EWS سیستم F&G ازEWS سیستم ESD جدا شده و برای E/OWS ،F&G در نظر گرفته شود. |  | 01/2294/55898 | 1401/02/20 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
3 | ارتباطModbus بین F&G و DCS دیده شود. |  | 01/2294/55898 | 1401/02/20 | مدرک مطابق خواست کارفرمای محترم اصلاح گردید.
4 | در قالب Note اعلام گردد شبکه Modbus مورد استفاده از نوع Modbus RTU در نظر گرفته می شود. |  | 01/2294/55898 | 1401/02/20 | در قسمت legend نقشه، ارتباط Modbus بصورت Redundant Modbus RTU Serial Link ذکر شده است.
| اعلام گردد که شبکه ارتباطی پرینترها از شبکه مانیتورینگ متفاوت خواهد بود. |  | 01/2294/55898 | 1401/02/20 | در قالب Note در مدرک اعلام گردید که شبکه پرینترمتصل به DCS Engineering workstation از شبکه مانیتورینگ مستقل می باشد اما پرینترهای Operator workstation داخل شبکه مانیتورینگ می باشند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 17 Apr 2022 |  |  |  |  | Date: