## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-DW-0001_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0936 |  |  | Transmital Date: 11 May 2022
Document Title: Typical Instrument Installation Drawing - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-0936 |  |  | Transmital Date: 11 May 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DW-0001_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | سايز stand pipe ها، 3" در نظر گرفته شود |  | BK-SUR-ENG-INS-01-04471 | 2022-05-29 | اگر منظور مشاور کارفرما محترم از stand pipe همان support می باشد مطابق بند8.1 مدرک specification for instrumentation همه این ساپورت‌ها دارای سایز 2" می‌باشد در ضمن از آنجائیکه در P&ID-EXTENSION OF BINAK B/C MANIFOLD ، مخزنی ، درام یا وصلی وجود ندارد بنابراین نیاز به stand pipe نمی باشد
2
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 28 May 2022 |  |  |  |  | Date: