## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0004-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0861 |  |  | Transmital Date: 25-Apr-2022
Document Title: Calculation Note For UPS System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0861 |  |  | Transmital Date: 25-Apr-2022
[5 empty] | CRS No: NISOC--CRS- BK-GCS-PEDCO-120-EL-CN-0004-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت جلوگیری از over size شدن بی مورد دستگاه، تاکید گردد که این مدرک با توجه به بار واقعی و نهایی شده به روزرسانی گردد و در صورت نیاز، سایزینگ دستگاه توسط vendor اصلاح گردد. |  | 1401-2294-91107 | 1401-03-17 | این مدرک بر اساس آخرین لیست بار به روز رسانی شد. همچنینی در قسمت نتیجه بیان شده است که ازنده موظف است محاسبات را در صورت نیاز اصلاح نماید.
2 | درخصوص بند 6 مدرک Reply Sheet ، همان گونه که در کامنت قبلی این امور مشخص است، سطح ولتاژ 93 ولت صرفا جهت اطلاع در طراحی دستگاه ups توسط سازنده می باشد بنابراین لازم است در نرم افزار سایزینگ باتری، همان سطح ولتاژ 1.14v برای هر سلول باتری در نظر گرفته شود. |  | 1401-2294-91107 | 1401-03-17 | مطابق با جدول بخش 5 از مدرک، ولتاژ نهایی هر باتری مقدار 1.136 در نظر گرفته شده است. همچنین در ادامه نوت بخش 7 عنوان گردید که سطح ولتاژ طراحی ups می بایست 93 ولت توسط سازنده در نظر گرفته شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 09-May-22 |  |  |  |  | Date: