## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0011-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0590 |  |  | Transmital Date: 13-Feb-2022
Document Title: Calculation Note for Capacitor Banks |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0590 |  |  | Transmital Date: 13-Feb-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0011-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در بخش 4.2، پیرو نامه شماره 413209 مورخ 1400/11/28 جهت خازن های فشار متوسط الکتروموتور کمپرسورهای گاز تمهیدات لازم جهت حفاظت مدارات خازن شامل: فیوز، دیسکانتکت سوییچ، و .. در نظر گرفته شود. |  | 1400-2294-430282 | 1400-12-09 | موارد در مدرک دیاگرام تک خطی لحاظ خواهد شد.
2 | پیرو مذاکرات تلفنی در خصوص حذف بانک خازنی مربوط به پمپ آب آتش نشانی پیشنهاد و دلایل فنی ارائه گردد. |  | 1400-2294-430282 | 1400-12-09 | مطابق با مذاکرات تلفنی صورت پذیرفته با کارفرمای محترم مقرر گردید به دلیل استفاده از پمپ آب آتش نشانی در شرایط اضطرار، بانک خازنی مربوط به این پمپ حذف گردد. از طرفی وجود بانک خازنی ممکن است در عملکرد صحیح پمپ در حال اضطرار، تأثیر منفی نیز بگذارد. لذا بان خازنی حذف گردیده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 27-Feb-22 |  |  |  |  | Date: