## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0652 |  |  | Transmital Date: 27-Feb-2022
Document Title: Data Sheets For Capacitor Bank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0652 |  |  | Transmital Date: 27-Feb-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 2.3 : حداکـثر دمای محیط مطابق مکاتبات قبلی اصلاح شود. |  | 1400-2294-447230 | 1400-12-22 | مطابق با کامنت دریافتی از آن کارفرمای محترم بر روی نامه شماره 94378 مورخ 1401/03/18، ماکزیمم دمای محیطی 52 درجه سانتی گراد در نظر گرفته شده است.
2 | بند3.6: مقدار ظرفیت آمپر باسبار بانک خازنی مطابق بانک خازنی اصلاح گردد. |  | 1400-2294-447230 | 1400-12-22 | مطابق مدرک محاسبات اصلاح گردید.
3 | بند 8.4 : قید گردد ولتاژ 230VAC مدار کنترل از طریق ترانس ایزوله تامین می گردد. |  | 1400-2294-447230 | 1400-12-22 | همانطور که در مدرک تیپیکال سر چاهی ذکر شده است، ولتاژ مدار کنترل از طریق ترانس ایزوله هر cubicle می باشد، با این حال نوت شماره 2 مربوط به این موضوع در مدرک اضافه گردید.
4 | بند 9.3 : جریان مجاز کلید ورودی تابلوی بانک خازنی اصلاح گردد. |  | 1400-2294-447230 | 1400-12-22 | مطابق مدرک محاسبات اصلاح گردید.
5 | بند 11.1 : عبارت است Space Heater به Space heater with thermostat تغییر یابد. |  | 1400-2294-447230 | 1400-12-22 | اعمال گردید.
6 | بخش 9 مربوط به کلید ورودی با توجه به نامه 00/2294/443266 مورخ 1400/12/19 می بایست شفاف سازی گردد. |  | 1400-2294-447230 | 1400-12-22 | مورد ذکر شده در دست بررسی بوده و به زودی پاسخ داده خواهد شد.
7 | شماره گذاری F-NUMBER انجام شده، می بایست مطابق نامه 00/2294/421733 مورخ 1400/12/03 انجام پذیرد. |  | 1400-2294-447230 | 1400-12-22 | شماره گذاری مدرک براساس توافقات انجام شده با آن کارفرمای محترم مطابق با MDL پروژه اعمال شده است.
8 | جهت دیتا شیت بانک خازنی فشار ضعیف، کلیه موارد بجز آیتم 6 لحاظ گردد. |  | 1400-2294-447230 | 1400-12-22 | در نظر گرفته خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Mar-22 |  |  |  |  | Date: