## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0005-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0379 |  |  | Transmital Date: 26-Dec-2021
Document Title: UPS Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0379 |  |  | Transmital Date: 26-Dec-2021
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0005-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لازم است جهت به حداقل رساندن ویرایش ها، این مدرک از نظر کلیات و جزِئیات با نقشه SLD مرجع و مورد تایید این امور که در فایل پیوست میباشد مقایسه، بازنگری و به روز رسانی گردد. |  | 1400-2294-375310 | 1400-11-02 | فایل ارسالی آن کارفرمای محترم مورد استفاده قرا گرفت و بر اساس آن، این مدرک به روزرسانی شد.
2 | لازم است در صورت نیاز مقادیر توان، رنج دستگاه و آمپر ساعت باتری ها با توجه به آخرین ویرایش های تایید شده مدارک سایزینگ به روز رسانی گردد. |  | 1400-2294-375310 | 1400-11-02 | در نوت شماره 8 اشاره گردید که سایز تمامی اداوت الکتریکی می بایست توسط سازنده صورت پذیرد.
2-1 | پاسخ آن شرکت در بند 2 ریپلای شیت مبنی بر دمای طراحی 48 درجه سانتی گراد مورد تایید نیست. مطابق با مکاتبات قبلی جهت طراحی تجهیزات الکتریکی بر اساس Spec پایه پروژه در بخش شرایط محیطی، ملاک طراحی بدترین حالت قید شده در مدرک فرآیندی BEED می باشد. لذا لازم است که دماهای ذکر شده بر این اساس اصلاح گردند. |  | 1400-2294-375310 | 1400-11-02 | مطابق با نامه های آن کارفرمای محترم به شماره 94378 مورخ 1401/03/18 بشینه دمای تجهیزات الکتریکی 52 درجه سانتی گراد می باشد. لذا این عدد ملاک طراحی در نظر گرفته شده است و در داده برگه مدارک لحاظ شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 04-Jan-22 |  |  |  |  | Date: