## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0662 |  |  | Transmital Date: 02-Mar-2022
Document Title: Capacitor Banks Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0662 |  |  | Transmital Date: 02-Mar-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به ثابت بودن کلید MCCB در تابلو های بانک خازنی، حالت Test چگونه ایجاد می شود و چرا فقط در یک سمت MCCB حالت کشویی نشان داده شده است. |  | 1401-2294-16106 | 1401-01-20 | با توجه به Fix بودن تابلوی بانک خازنی مدرک فوق اصلاح گردید.
2 | چراغ سگنال برای حالت Test نیازی نمی باشد. |  | 1401-2294-16106 | 1401-01-20 | مطابق با کامنت شماره یک حذف گردید.
3 | به جای MCCB از کلید ACB با حفاظت مناسب استفاده گردد.. |  | 1401-2294-16106 | 1401-01-20 | مطابق با محاسبات انجام شده جریان بانک خازنی با ظرفیت 120 کیلووار، حدود 173 آمپر بوده که با احتساب 1.5 برابر جریان نامی، 250 آمپر خواهد شد. در نتیجه آن کلید انتخابی 315 آمپر است. و از اینرو نیاز به در نظگرفتن کلید ACB نمی باشد. کلیدهای MCCB تا جریان 400 آمپر میتوان استفاده نمود.
4 | برای خطاهای ولتاژی چراغ سیگنال مجزا استفاده شود. |  | 1401-2294-16106 | 1401-01-20 | خطاهای ولتاژی و خطاهای جریانی برای کلید ورودی به صورت مجزا در نظر گرفته شده است.
5 | نماد حفاظت های MCCB و رنج تنظیمات آن نشان داده شود. |  | 1401-2294-16106 | 1401-01-20 | این کلید LSIG است بدین صورت L: 49 S:51 I:50 G:50G لذا تمام حفاظت ها مورد نیاز وجود دارد.
6 | محل نصب PT باید قبل از کلید باشد و ولتاژ سر کابل را نشان دهد. |  | 1401-2294-16106 | 1401-01-20 | محل نصب PT به قبل از کلید منتقل شد.
7 | تمام فیوز های پله های خازن مجهز به استریکر پین و چراغ سیگنال مجزا برای حالت خطا باشد. |  | 1401-2294-16106 | 1401-01-20 | استریکر پین و چراغ سیگنال خطا اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 12-Mar-22 |  |  |  |  | Date: