## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0011-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0590 |  |  | Transmital Date: 13-Feb-2022
Document Title: Calculation Note for Capacitor Banks |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0590 |  |  | Transmital Date: 13-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0011-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised base on comments on load list and shall be submitted as IFA after finalizing or minor comments on load list. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | بر اساس تغییرات در مدرک Process Electrical Load List مدرک لیست بار برق به روز رسانی گردید و به تبع این مدرک نیز ویرایش گردید |  |  | Will be checked later.
2 | Capacitor bank sizing for fire fighting pump shall be added. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | اعمال گردید. |  |  | See below item 4.
3 | According to basic electrical load list, a cofficient of 0.6 shall be considered in LV capacitor bank sizing. |  | BK-SUR-ENG-ELE-00-02183 | 2021-12-04 | اعمال گردید. |  |  | Noted and Closed.
4 | Ref. item2 above: Absorbed Peak Active/Reactive Power (Kw) shall be modified base on latest revision of of load list and so fire water pump capacitor bank calculation shall be revised. |  | BK-SUR-ENG-ELE-00-03236 | 2022-02-27 | توان اکتیو و راکتیو دریافتی با توجه آخرین رویژن لیست بار بروز رسانی گردید.
5 | Calculation for LV Capacitor Bank: Q_L= 693 × (0.61-0.32)=201 Kvar, not 204 KVAR |  | BK-SUR-ENG-ELE-00-03236 | 2022-02-27 | با توجه به تغییرات مرتبط با توان اکتیو و راکتیو محاسبات مربوط نیز بروزرسانی گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 27-Feb-22 |  |  |  |  | Date: