## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0861 |  |  | Transmital Date: 25-Apr-2022
Document Title: Data Sheets For UPS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0861 |  |  | Transmital Date: 25-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0001-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on following documents: -Calculation note for AC UPS system -AC UPS single line diagram -Cable list and related rows such as rated power Inverter/by pass transformer, cable size, etc shall be modified base on above mentioned document. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | مطابق با ترنسمیتال شماره 852، مدرک لیست بار ابزار دقیق و پس از بازدید انجام شده، مورد بانگری قرار گرفت و این مدرک ملاک انجام محاسبات UPS می باشد. با این وجود هر گونه تغییر در مدارک ابزاردقیق، در ویرایش های بعدی این مدرک منعکس خواهد شد. |  |  | Will be checked later.
2 | Item 2, Environmental Conditions: Shall be modified base on latest revision of process baisis of design. Elevation from sea level ~ 12.5 m Min. Absolut air temperature(°C): 3.24 °C Max. Absolut air temperature(°C): 49.36 °C Max. Relative Humidity: 60.52% |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | دماهای مورد نیاز بر اساس آخرین ویرایش مدرک فرآیند به شماره ترنسمیتال 700، به روزرسانی گردید. همچنین فایل ارسالی کارفرمای محترم ملاک برگه داده UPS قرار گرفته است. |  |  | Noted and Closed.
3 | Item 9, Installation: The UPS and battries will be installed indoor in control building, not outdoor, under shelter.!!! |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در بند 4 اصلاح گردید. |  |  | Noted and Closed.
4 | Item 15, Noise Level: The noise level measured at one meter from the UPS unit/s shall not exceed 60 dB (A) at any load. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در بند 11 اصلاح گردید. |  |  | Noted and Closed.
5 | Item 18, Degree of protection: Degree of protection shall be modified IP42, instead of IP31. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در بند 14 اصلاح گردید. |  |  | Noted and Closed.
6 | Item 30, Grounding system: Earthing system shall be modified "IT" instead of solidly earthed neutral. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در بند 27 و 30 اصلاح گردید. |  |  | Noted and Closed.
7 | Item 61, Stand Type: Anti seismic shall be added. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در بند 58 اصلاح گردید. |  |  | Noted and Closed.
8 | Item 131, Serial Communication Capability: Type of connection shall be specified. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | مطابق با کامنت های مشابه از RS 485 استفاده گردید. |  |  | Noted and Closed.
9 | Tag of AC UPS shall be added and specified. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | در ابتدای مدرک اعمال گردید. |  |  | Noted and Closed.
10 | Use attached sample data sheet for next revision with considering above mention comments. |  | BK-SUR-ENG-ELE-00-02560 | 2022-01-04 | از فایل پیوستی استفاده شد و مدرک به روزرسانی گردید. |  |  | Noted and Closed.
11 | با توجه به نامه شماره 47232 مورخ 1401/02/11 (پاسخ ذينفع اصلي پروژه به ترنسميتال 852) مبني بر عدم تاييد مدرك I&C Power consumption و همچنين نقطه نظر واحد ابزاردقيق پترو ايران به شرح زير، امكان بررسي ارقام درج شده در مدرك حاصل از خروجي محاسبات در اين مقطع وجود نداشته و لذا مقتضي است پيرو مذاكرات قبلي تا زمان نهايي شدن مدرك مذكور از ارسال مجدد اين مدرك خودداري شود. -با توجه به نهايي نشدن مدرك I&C Power consumption و نقطه نظرات موجود در فايل ضميمه T-0861 ميزان بار مورد نياز تجهيزات ابزاردقيق نهايي نمي باشد. |  | BK-SUR-ENG-ELE-01-04178 | 2022-05-09 | مدرک بر اساس بازدید انجام شده در فروردین ماه و مذاکرات صورت گرفته در بخش ابزاردقیق به روزرسانی گردید. با این وجود در صورت هرگونه تغییر در آینده، ویرایش جدید مدارک تولید خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 09-May-22 |  |  |  |  | Date: