## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0002-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0481 |  |  | Transmital Date: 19-Jan-2022
Document Title: Data Sheets For DC Charger |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0481 |  |  | Transmital Date: 19-Jan-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0002-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on following documents: -Calculation note for DC charger system -DC charger single line diagram -Cable list and related rows such as rated charger output current, cable size, etc shall be modified base on above mentioned document. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | مدرک محاسباتی باتری شارژر مورد بازبینی قرارگرفت و مطابق با آن، تغییرات در این دیتاشیت لحاظ گردید. |  |  | See below item 11
2 | There is conflict between this document and calculation note for DC charger system for example calculated No. of batteries per each bank and total quantity of cells for 24VDC are 19 and 38 while in data sheet has been mentioned 38 and 76. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | مدرک محاسباتی باتری شارژر مورد بازبینی قرارگرفت و مطابق با آن، تغییرات در این دیتاشیت لحاظ گردید. |  |  | Noted&Closed.
3 | Item 5.16, Earthing system: Earthing system shall be modified "IT" instead of solidly earthed neutral. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | در آیتم 5.16 نحوه سیستم زمین به IT تغییر یافت |  |  | Noted&Closed.
4 | Item 4.3, Rated Output Power (kW): Shall be modified to "As per Load Profile" not rated power(KW) and shall be added at the end of document with interval time. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | نمودار مصرف توان DC در این مدرک اضافه گردید. |  |  | Noted&Closed.
5 | Item 4, DC Output: "Rated charger output current" shall be added as a new row and shall be specified base on calculation. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | تغییرات با توجه به مدرک جدید دریافتی از کارفرمای محترم اعمال گردید |  |  | Noted&Closed.
6 | Item 6.39, Stand Type: Shall be modified to anti seismic stand. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | در آیتم 8.4 از دیتاشیت پایه های باتری ضدزلزله در نظر گرفته شد. |  |  | Noted&Closed.
7 | Item 7.18&7.25, Incoming/Outgoing Circuit breakers: Number of pole shall be added and specified for incoming and outgoing CB. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | همانطور که در دیاگرام تک خطی اشاره شد، برخی از پارامترها را سازنده تعیین می کند. |  |  | Noted&Closed.
8 | Item 6.8, Battery type: SBL shall be added. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | نوع باتری های SBL است. |  |  | Noted&Closed.
9 | Tag of DC chargers shall be added and specified. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | در آیتم 1.15 این موضوع عنوان شد |  |  | Noted&Closed.
10 | Use attached sample data sheet for next revision with considering above mention comments. |  | BK-SUR-ENG-ELE-00-02474 | 2021-12-28 | اعمال گردید |  |  | Noted&Closed.
11 | Ref. item 1 above: This document shall be revised after finalizing DC UPS calculation specially for 24Vdc system. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | این مدرک بر اساس آخرین لیست بار بخش ابزاردقیق به روزرسانی شد.
12 | 110VDC and 24VDC load profiles shall be modified. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | پروفیل بار شارژر 24 و 110 به روزرسانی گردید.
13 | According to our telephone conversation, in some cells such as 3.8,4.6,4.7 and etc. , editing corrections shall be implemented. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید
14 | check boxes in both native and pdf files have not adjusted in correct location and need to modify. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید
15 | This document shall be revised and reissued just in case of prerequisite documents such as F&G power consumption list and profile issued based on Vendor recommendation. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | در صورت وجود هر گونه تغییر آینده در مدارک بخش ابزاردقیق، این مدرک به روزرسانی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Jan-22 |  |  |  |  | Date: