## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0007_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0652 |  |  | Transmital Date: 27-Feb-2022
Document Title: Data Sheets For Capacitor Bank |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0652 |  |  | Transmital Date: 27-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0007_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be modified and finalizing base on network study, single line diagram for capacitor bank and capacitor bank sizing. (If Required) |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | تمامی مدارک بانک خازنی مورد ویرایش قرار گرفت.
2 | It shall be clarified why fire water pump capacitor bank has not been considered in document. At this stage this document shall not be revised before receiving comments on capacitor bank calculation document. In other word fire water pump capacitor bank deleted after receiving the approval of client. |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | مطابق با مذاکرات تلفنی صورت پذیرفته با کارفرمای محترم مقرر گردید به دلیل استفاده از پمپ آب آتش نشانی در شرایط اضطرار، بانک خازنی مربوط به این پمپ حذف گردد. از طرفی وجود بانک خازنی ممکن است در عملکرد صحیح پمپ در حال اضطرار، تأثیر منفی نیز بگذارد. لذا بان خازنی حذف گردیده است.
3 | Type and size of control cable/s shall be specified.(For example sample voltage and current and interlock with diesel generator.) |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | در ردیف 5 از بند 4 اضافه گردید.
4 | Page 3&6, Item 3.6/Page 5&8, Item 9.3: It seems the rated current of bus bar and CB has not been selected correctly as below calculation: 600KVAR/(1.732*11)=32, 72*1.5=48A 120KVAR/(1.732*0.4)=173, 72*1.5=260A |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | حداقل باسبار تابلوهای MV برابر 630 آمپر و برای تابلوهای LV مربوط به خازن این پروژه 315 آمپ در نظر گرفته شده است.
5 | Page 6, Item 3.7/Page 8, Item 9.4: Rated short circuit level shall be rechecked and modified. Short circuit level shall be modified after finalizing or minor comments on Electrical Network (Load Flow, Motor Starting & Short Circuit) Study Report |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | مطابق با مطالعات شبکه برق و ترنسمیتال 1082 سطح اتصال کوتاه بارهای LV در ایستگاه تقویت فشار گاز 24 کیلو آمپر می باشد. لذا جهت حاشیه امنیت سطح اتصال کوتاه برای خازن MV برابر 25 و برای خازن LV برابر 31.5 کیلو آمپر در نظر گرفته شده است.
6 | Page 8, Item 9.2: The MCCB shall be selected Fixed type instead of withdrawable type. |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | اعمال گردید.
7 | Page 5&8, Item 9.7: Voltage protection shall be added. |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | اعمال گردید.
8 | Page 5, Item 9.2: According to our telephone conversation, there is conflict between this document and single line diagram for capacitor bank from point of view tripping device (HRC or VCB) and shall be modified. |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | کنتاکتور سوییچ به همراه فیوزهای HRC در نظر گرفته شده است.
9 | Rated insulation voltage shall be added and specified. |  | BK-SUR-ENG-ELE-00-03418 | 2022-03-08 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 08-Mar-22 |  |  |  |  | Date: