## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SUMMARY
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0007 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
I&C POWER CONSUMPTION SUMMARY نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | APR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708973
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0007 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 |  | X | [6 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCES
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D01
REFERENCE DOCUMENTS:
| I/O LIST FOR CONTROL SYSTM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0002
| I/OLIST FOR ESD SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0003
| I/O LIST FOR F&G SYSTEM | [7 empty] | BK-GCS-PEDCO-120-IN-LI-0004
| SPECIFICATION FOR INSTRUMENTATION | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| SPECIFICATION FOR CONTROL SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0002
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0003
| SPECIFICATION FOR ESD SYSTEM | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0012
| SPECIFICATION FOR INSTRUMENT AND CONTROL OF PACKAGE UNIT SYSTEM(PU | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0004
D01

## UPS 110VAC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI |  | 0007 | D01
INST./CONTROL UPS 110 VAC POWER CONSUMPTION TABLE
- Table (1) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION (KW)
| 1 | DCS SYSTEM PANEL (INCLUDING NETWORK SWITCHES) |  |  | 1 | 2 hr. | 400 |  | 0.8 |  |  | 2 Nos. (Redundant) |  | 3.8
| 2 | DCS MARSHALLING PANEL |  |  | 3 |  |  |  | 1
| 3 | ESD SYSTEM PANEL |  |  | 1 | 2 hr. | 200 |  | 0.8 |  |  | 2 Nos. (Redundant) |  | 2.8
| 4 | ESD MARSHALLING PANEL |  |  | 2 |  |  |  | 1
| 5 | ELECRO GAS COMPRESSOR UCP SYSTEM CABINET |  |  | 1 | 2 hr. | 450 |  | 0.8 |  |  | 2 Nos. (Redundant) |  | 4.8
| 6 | ELECRO GAS COMPRESSOR UCP MARSHALING CABINET |  |  | 4 |  |  |  | 1
| 7 | DEHYDRATION PACKAGE LCP/ANALYZER |  |  | 1 | 2 hr. | 20 |  | 0.5 |  |  | 2 Nos. (Redundant) | 1 | 0.5
| 8 | PAGING SYSTEM |  |  | 1 | 2 hr. | - |  | 1 |  |  | 2 Nos. (Redundant) | 1 | 1
| 9 | AIR COMPRESSOR LCP |  |  | 2 | 2 hr. | 2x100 |  | 0.8 |  |  | 2 Nos. (Redundant) | 2 | 1.6
| 10 | NITROGEN PACKAGE LCP |  |  | 2 | 2 hr. | 2x100 |  | 0.8 |  |  | 2 Nos. (Redundant) | 2 | 1.6
| 11 | OPERATOR WORKSTATION (INCLUDING DCS, ESD / F&G, PACKAGE OWSs) |  |  | 4 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 2.4
| 12 | DCS ENGINEERING WORKSTATION |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
| 13 | ESD ENGINEERING WORKSTATION |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
| 14 | F&G ENGINEERING WORKSTATION |  |  | 1 | 2 hr. | - |  | 0.6 |  |  | 1 No. ( Socket) | 4 | 0.6
|  |  | TOTAL POWER CONSUMPTION (KW) | [10 empty] | 20.3
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW) | [10 empty] | Note 6
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Printers and larg screen will be supplied by normal Electrical power. Note 3:
Note 3: UPS power for HVAC Panel shall be supplied by vendor. Only 400VAC , 3 phase will be supplied by EPC contractor. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003.
Note 5 : UPS of CCTV panel is nit considered since will be provided by vendr. Note 6: Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be considered in UPS battery sizineg by electrical .
D01
D01
D01

## NON UPS 230VAC
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0007 | D01
INST./CONTROL NON- UPS 230 VAC POWER CONSUMPTION TABLE
- Table (2) is represents AC UPS power consumption for inst./control system. The estimation is based on the design of control systems, comprising of various equipment located in Control Room.
| ITEM | DESCRIPTION |  |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  |  |  | QTY. (Note 1) | TOTAL POWER CONSUMPTION (KW)
| 1 | Cabinet Utilities For PCS (Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 4 | 0.64
| 2 | Cabinet Utilities For ESD (Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 3 | 0.48
| 3 | Cabinet Utilities For F&G (Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 3 | 0.48
| 4 | Cabinet Utilities For Gas Compressor UCP(Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 5 | 0.8
| 5 | Cabinet Utilities For Total Flooding UCP(Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 1 | 0.16
| 6 | Cabinet Utilities For Paging Cabinet (Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 1 | 0.16
| 7 | Cabinet Utilities For Air Compressor LCP(Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 2 | 0.32
| 8 | Cabinet Utilities For Nitrogen package LCP(Heater, Socket, Fan , Light) |  |  | 0.16 |  |  |  |  | 2 | 0.32
| 9 | Control Desk Sockets |  |  | 0.5 |  |  |  |  | 7 | 3.5
| TOTAL POWER CONSUMPTION | [9 empty] | 6.86
|  |  | TOTAL POWER CONSUMPTION (KW) | [7 empty] | 6.86
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW) | [7 empty] | Note 2
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be considered by electrical .
D01
D01
D01

## 24 VDC CHARGER
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I&C POWER CONSUMPTION SAMMARY
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK | GCS |  | PEDCO | 120 |  | IN | LI |  | 0007 | D01
INST./CONTROL UPS 24 VDC POWER CONSUMPTION TABLE
- Table (3) is represents 24V DC UPS power consumption for F&G system. The estimation is based on the design of F&G systems, comprising of various equipment located in Control Room/Field.
| ITEM | DESCRIPTION |  |  | PANEL QTY (Note 1) | BACK UP TIME | ESTIMATTED I/O (NOTE 4) |  | UNIT POWER CONSUMPTION (KW) (Note 1) |  |  | FEEDER QTY |  | TOTAL POWER CONSUMPTION FOR QUIESENCE MODE(KW) |  | TOTAL POWER CONSUMPTION FOR ALARM MODE (KW)
| 1 | F&G SYSTEM PANEL |  |  | 1 | 24hr. | 130 |  | 0.6 ( for Quiescence& Alarm mode) |  |  | 2 Nos. (Redundant) |  | 0.6+(0.1 x 2) = 0.8 KW for 24hr (Note 3) |  | -
| 2 | F&G MARSHALLING PANEL |  |  | 2 | 24hr. |  |  | 0.1 (for Quiescence mode)
[6 empty] | 5 MIN |  |  | 0.8 (for alarm mode) |  |  |  |  | - |  | 0.6+(0.8x 2) = 2.2 KW for 5 Min (Note 3)
| 1 | FACP system |  |  | 1 | 24hr. | 70 |  | 0.3 ( for Quiescence& Alarm mode) |  |  | 2 Nos. (Redundant) |  | 0.3+(0.05 x 1) = 0.305 KW for 24hr (Note 3) |  | -
| 2 | FACP Detectors |  |  |  | 24hr. |  |  | 0.05 (for Quiescence mode)
[6 empty] | 5 MIN |  |  | 0.5 (for alarm mode) |  |  |  |  | - |  | 0.3+(0.5 x 1) = 0.8 KW for 5 Min (Note 3)
| 3 | FIRE PROTECTION AND TOTAL FLOODING SYSTEM UCP |  |  | 1 | 5 MIN | 50 |  | 0.8 |  |  | 2 Nos. (Redundant) | 2 | - |  | 0.8 KW for 5 Min (Note 3)
|  |  | TOTAL POWER CONSUMPTION FOR 5 MIN BACK UP TIME (KW) | [10 empty] | 3.8 (Note 3)
|  |  | TOTAL POWER CONSUMPTION FOR 24 HOURS BACK UP TIME (KW) | [10 empty] | 1.105 (Note 3)
|  |  | TOTAL POWER CONSUMPTION CONSIDERING SPARE CAPACITY (KW) | [10 empty] | Note 2
Note 1 : Shall Be Finalized After Purchase Through Vendor Final Documents. Note 2: Spare capacity has not been considered in I&C power consumption calculation. Required spare shall be considered by electrical . Note 3: DC charger shall supply 1KW + Spare, for 24H back up time but also it shall be capable to prepare 3.8KW+ Spare, as a peak power consumption in alarming conditions for 5 Min back up time. it shall be considered during battery sizing in related documents. Note 4: Power Consumption of panels have been estimatted considering project I/O count. Refer to '' I/O List For Control System Doc.No.BK-GCS-PEDCO-120-IN-LI-0002 , I/O List For ESD System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003 , I/O List For F&G System Doc.No.BK-GCS-PEDCO-120-IN-LI-0003.
D01
D01
D01