## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0006-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0481 |  |  | Transmital Date: 19-Jan-2022
Document Title: DC Charger Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0481 |  |  | Transmital Date: 19-Jan-2022
[5 empty] | CRS No:NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0006-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نمای های تک خطی مورد تایید می باشند. پیشنهاد می شود موارد زیر در SLD در نظر گرفته شود: |  | 1400-2294-412403 | 1400-11-27
2 | تغذیه AC ورودی دستگاه های باتری شارژر (DC-UPS) باید از باس اضطراری تامین گردد. |  | 1400-2294-412403 | 1400-11-27 | طبق استاندارد IPS جهت قابلیت اطمینان بر روی شبکه در صورت بروز خطا بر روی کوپلرC و یا باس اضطراری، یکی از شارژرها روی باس نرمال و یکی روی باس اضطراری قرار میگیرد. بدین سان در این پروژه نیز این موضوع مد نظر میباشد.
2 | به منظور قابلیت اطمینان سیستم های DC-UPS، لازم است در مدارات Diode Droper، از کنتاکت های N.C استفاده گردیده و این مورد در SLD مشخص گردد. |  | 1400-2294-412403 | 1400-11-27 | طبق نظر کارفرما کنتاکت N.C استفاده گردیده و مورد فوق در نقشه SLD اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Jan-22 |  |  |  |  | Date: