## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0006-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0481 |  |  | Transmital Date: 19-Jan-2022
Document Title: DC Charger Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0481 |  |  | Transmital Date: 19-Jan-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0006-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on DC charger calculation and cable sizing documents. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مدرک محاسباتی باتری شارژر مورد بازبینی قرارگرفت و مطابق با آن، تغییرات در این مدرک لحاظ گردید. |  |  | See below item 10
2 | Single line diagram for 24VDC and 110VDC shall be considered separately in this document because according to basic design criteria (Appendix 1&3), both of them has the same configuration but the outgoing feeders, charger size, etc are different from each other. Meanhile note 2 shall be deleted. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید و نقطه نظر شماره 2 حذف گردید. |  |  | Noted&Closed.
3 | According to scope of work, all existing and new MV and LV switchgear DC loads shall be fed by new 110VDC UPS, so the 110DC UPS outgoing feeders shall be modified. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مطابق با مذاکرات انجام شده، فیدرهای خروجی تابلوی توزیع DC مورد بازبینی قرار گرفت. |  |  | Noted&Closed.
4 | Some technical characteristics of equipment shall be added and specified on single line diagram such as rated charger size, rated voltage/short circuit level/rated current/Incoming CB size of DC distribution board, "Exd IIC T3" for fuse box, capacity/back up time/number and type of battery, size of CB and Transformers, the cable size and type between fuse box and battery/fuse box and UPS/Incoming and outgoing feeders, voltmeter and ammeter range and outgoing feeder power. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | مطابق با مذاکرات انجام شده، برخی از پارامترهای اصلی مشخص گردید. سایزینگ برخی ادوات نیز به سازنده واگذار شد. |  |  | See below item 11
5 | Following items shall be added as notes: - Interlocks will be provided to inhibit battery boost charge if battery room ventilation is out of service. -Automatic battery isolation facility shall be provided for incoming MCCB of battery bank. incoming MCCB of battery bank shall be open when F&G system send battery insulation signal to the UPS. -An earth fault monitoring shall be considered for every 10 feeders for easy of finding faulty branch. -Metering and protection system shall be completed based on ac ups specification and detailed information shall be indicated On vendor drawing. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید. |  |  | Noted&Closed.
6 | As per baisc design criteria appendix 1 and 3 surge arrester shall be considered for incomings. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | اعمال گردید. |  |  | Noted&Closed.
7 | According to basic electrical design criteria (Appendix 1&3) PT ( 400/110) with suitable fuse shall be considered for incoming voltmeters. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمال گردید. |  |  | Noted&Closed.
8 | The body of DC charger panel shall be earthed directly from two point. It shall be shown. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمل گردید. |  |  | Noted&Closed.
9 | The symbol of MCCB and MCB for incoming and outgoing feeders of DC distribution board shall be different from each other in single line diagram. |  | BK-SUR-ENG-ELE-00-02471 | 2021-12-28 | بر اساس کامنت کارفرمای محترم، پیکربندی سیستم DC تغییر پیدا کرد و موارد بر روی مدرک اعمل گردید. |  |  | Noted&Closed.
10 | Ref. item 1 above: This document shall be revised base on comment on DC UPS calculation. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | پیرو مذاکرات انجام شده در جلسات با کارشناسان کارفرما و شرکت پترو ایران، ترنسمیتال 852 ملاک طراحی بخش برق قرار گرفته است و در نتیجه آن، ویرایش جدید مدارک DC CHarger (محاسبات، تک خطی و داده برگ) تولید خواهد شد
11 | Ref. item 4 above: Rated busbar current of distribution panel shall be specified. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید.
12 | Feeder for emergency bus (New/Existing) shall be considered seperatly. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید.
13 | Some rows such cable size, type and tag shall be added for tables below distribution panels and shall be filled base on cable list. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | اعمال گردید.
14 | This document shall be revised and reissued just in case of prerequisite documents such as F&G power consumption list and profile issued based on Vendor recommendation. |  | BK-SUR-ENG-ELE-00-02888 | 2022-01-31 | بعد از نهایی شدن قرارداد با وندور، لیست بار سیستم f&g مورد بازنگری قرار خواهد گرفت و در صورت وجود هر گونه تغییر، مدرک ویرایش میگردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 31-Jan-22 |  |  |  |  | Date: