## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-LD-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0817 |  |  | Transmital Date: 16-Apr-2022
Document Title: Control Logic Diagram For LV Incomers and bus tie |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0817 |  |  | Transmital Date: 16-Apr-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-LD-0001-D01 (1) |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 2 از 9 : کلید ورودی دیزل به MCC (کلیدQ4) می بایست به صورت NC نمایش داده شود. |  | 1401-2294-54910 | 1401/02/19 | مطابق با مذاکرات انجام شده کلید بعد از تابلو دیزل ژنراتور (ورودی به سوییچگیر) به صورت NC در نظر گرفته شد.
2 | مود عملیات ترانسفر دستی مطابق مدرک SPEC پروژه جهت کلید های Q1,Q2,Q3 با استفاده از رله سنکرون چک (رله 25) نمایش داده شود. |  | 1401-2294-54910 | 1401/02/19 | تغییرات مربوط به اضافه شدن رله سنکرون چک اعمال گردید.
3 | مطابق نقشه نمونه ارسالی با نامه شماره 301373 مورخ 1400/09/13 در بالای هر صفحه نمای کلی مربوط به وضعیت کلیدها و باس ها نمایش داده شود. |  | 1401-2294-43191 | 1401-02-08 | اعمال گردید.
4 | جهت هر صفحه ، عنوان عملیات انجام شده در آن صفحه در پایین نقشه قید گردد، به عنوان مثال : در صفحه 3 از 9 عبارت Q1 Closing & Opening درج گردد. |  | 1401-2294-43191 | 1401-02-08 | اعمال گردید.
5 | حفاظت TCS در مدرک جهت مدار بستن کلید اعمال شود. |  | 1401-2294-43191 | 1401-02-08 | اعمال گردید.
6 | نقطه نظرات تکمیلی متعاقبا ارسال می گردد. |  | 1401-2294-43191 | 1401-02-08 | در صورت دریافت نقطه نظرات تکمیلی، این مدرک بروزرسانی می شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 26-Apr-22 |  |  |  |  | Date: