## MTO
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Length (m) | Cable Type
|  |  |  | From | To
1 | D00 | NO-DP | 0.4 | Main distribution panel | Nisoc office building panel | 124.706 | 3x185+95 | 75 | CU/XLPE/SWA/PVC
2 | D00 | NR-DP | 0.4 | Main distribution panel | Nisoc residental building panel | 138.28 | 3x185+95 | 100 | CU/XLPE/SWA/PVC
3 | D00 | PO-DP | 0.4 | Main distribution panel | Petro office building panel | 86.28 | 3x95+50 | 60 | CU/XLPE/SWA/PVC
4 | D00 | PR-DP | 0.4 | Main distribution panel | Petro residental building panel | 86.28 | 3x120+70 | 75 | CU/XLPE/SWA/PVC
5 | D00 | RES-DP | 0.4 | Main distribution panel | Restaurant building panel | 78.28 | 3x95+50 | 65 | CU/XLPE/SWA/PVC
6 | D00 | DVR-DP | 0.4 | Main distribution panel | Driver building panel | 23.28 | 4x35 | 100 | CU/XLPE/SWA/PVC
7 | D00 | WR-DP | 0.4 | Main distribution panel | Warehouse panel | 7 | 4x10 | 90 | CU/XLPE/SWA/PVC
8 | D00 | WSH-DP | 0.4 | Main distribution panel | Workshop panel | 30 | 3x120+70 | 225 | CU/XLPE/SWA/PVC
9 | D00 | GH-DP | 0.4 | Main distribution panel | Gatehouse panel | 5 | 4x10 | 56 | CU/XLPE/SWA/PVC
10 | D00 | CMP-DP | 0.4 | Main distribution panel | Outdoor area panel | 22.5 | 4x35 | 50 | CU/XLPE/SWA/PVC
11 | D00 | CMP-DP-F01 | 0.23 | Outdoor area panel | Lighting pole-f01 | 1.25 | 3x4 | 175 | CU/XLPE/SWA/PVC
12 | D00 | CMP-DP-F02 | 0.23 | Outdoor area panel | Lighting pole-f02 | 0.75 | 3x4 | 90 | CU/XLPE/SWA/PVC
13 | D00 | CMP-DP-F03 | 0.23 | Outdoor area panel | Lighting pole-f03 | 0.5 | 3x4 | 35 | CU/XLPE/SWA/PVC
14 | D00 | CMP-DP-F04 | 0.23 | Outdoor area panel | Lighting pole-f04 | 1 | 3x4 | 75 | CU/XLPE/SWA/PVC
15 | D00 | CMP-DP-F05 | 0.23 | Outdoor area panel | Lighting pole-f05 | 0.75 | 3x4 | 115 | CU/XLPE/SWA/PVC
16 | D00 | - | 0.23 | pole junction box | Lighting fixture | 0.25 | 3x2.5 | 210 | CU/PVC/PVC
17 | D00 | - | 0.23 | Workshop panel | Lighting fixture | 0.75 | 3x2.5 | 35 | CU/PVC/PVC
18 | D00 | - | 0.23 | Workshop panel | Outlet socket | 1 | 3x4 | 35 | CU/XLPE/SWA/PVC
19 | D00 | - | 0.4 | Workshop panel | Welding socket | 37 | 4x35 | 35 | CU/XLPE/SWA/PVC