## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-EL-PY-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0428 |  |  | Transmital Date: 04-Jan-2022
Document Title: Lighting & Small Power Layout For Camp Area |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0428 |  |  | Transmital Date: 04-Jan-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-EL-PY-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | There is conflict between this document and cable route for camp area layout from point of view street cable size. It shall be clarify. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | هر دو مدرک مورد بازنگری قرار گرفتند و تناقضات برطرف گردید.
2 | A table for MTO shall be added in layout and all requiered items such as street light, flood light, socket and outdoor area lighting panels shall be specified in it. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | MTO تجهیزات مورد نیاز در جدول اضافه گردید. همچنین کابل ها در فایل اکسل مجزا به همرام نقشه مسیر کابل ارسال می گردد.
3 | Cable size shall be checked and modified especially for 3phase socket. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | براساس محاسبات کابل در مدارک سر چاهی، سایز کابل های مورد نیاز صورت پذیرفت. لازم به ذکر است مدرک لیست بار با ترنسمیتال شماره 970 تولید شده است.
4 | No. of Spare feeder for for NDP-CMP shall be modified base on used feeders and will be finalized in single line diagram. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | مدارک بروزرسانی گردید. همچنین دیاگرام تک خطی(علیرغم وجود آن در MDL) نشان داده شده است.
5 | Lighting fixturers for parkings will be fed from which feeders? Meanwhile above mentioned fixturers shall be shown in layout. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | برای روشنایی محوطه از چراغ های خیابانی استفاده شده است. که نور لازم را تامین می کند.
6 | There is conflict between note 4 and table below block diagrams from point of view type of cable between JB and lighitng fixturers. It shall be clarify. |  | BK-SUR-ENG-ELE-00-02677 | 2022-01-15 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 15-Jan-22 |  |  |  |  | Date: