## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-DT-0023 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0739 |  |  | Transmital Date: 3/28/2022
Document Title: Process Data Sheets For Closed Drain Pumps |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0739 |  |  | Transmital Date: 3/28/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-DT-0023_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | حداقل فشار ورودي به پمپ 0.2 بار نسبي در نظر گرفته شده كه صحيح نمي باشد لذا لازم است علاوه بر تصحيح موضوع فوق اختلاف فشار پمپ حداقل به ميزان 2 بار در نظر گرفته شود. |  | BK-SUR-ENG-PCS-01-03899 | 2022-04-13 | اعمال گردید.
2 | نقطه نظرات مرتبط، در خصوص مدرك محسبات هيدروليك در اين مدرك نيز اعمال گردد. |  | BK-SUR-ENG-PCS-01-03899 | 2022-04-13 | اعمال گردید.
3 | نشت بند انتخابي در برگه داده فني مكانيك بررسي مي گردد. |  | BK-SUR-ENG-PCS-01-03899 | 2022-04-13 | اعمال گردید.
4 | ضروريست نقطه نظرات ذينفع اصلي در خصوص مدرك مذكور اعمال گردد. |  | BK-SUR-ENG-PCS-01-03899 | 2022-04-13 | اعمال می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: