## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | LI | 0003 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | AUG.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | FEB.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | NOV.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708004
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0003 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | X | [5 empty] | 68
5 |  | X | X | [5 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | LI | 0003 | D02
REFERENCES:
| P&ID - EXTENSION OF BINAK B/C MANIFOLD | [5 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| P&ID - W007S | [5 empty] | BK-W007S-PEDCO-110-PR-PI-0002
| P&ID - W008N | [5 empty] | BK-W008N-PEDCO-110-PR-PI-0001
| P&ID - W018S | [5 empty] | BK-W018S-PEDCO-110-PR-PI-0001
| P&ID - W028 | [5 empty] | BK-W028-PEDCO-110-PR-PI-0001
| P&ID - W035 | [5 empty] | BK-W035-PEDCO-110-PR-PI-0001
| P&ID - W046S | [5 empty] | BK-W046S-PEDCO-110-PR-PI-0001
ABBREVIATIONS:
| I/O | INPUT / OUTPUT | [5 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
| DI: | DIGITAL INPUT SIGNAL | [5 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
| DO: | DIGITAL OUTPUT SIGNAL | [5 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
| AI: | ANALOGUE INPUT SIGNAL | [5 empty] | MCC: | MOTOR CONTROL CENTER
| AO: | ANALOGUE OUTPUT SIGNAL | [5 empty] | IRP: | INTERPOSING RELAY PANEL
| IND: | INDICATION | [5 empty] | CH: | CHANNEL
| STA: | STATUS | [5 empty] | ADD: | ADDRESS
| COM: | COMMAND | [5 empty] | TB: | TERMINAL BLOCK
| IS | INTRINSICALLY SAFE | [5 empty] | R: | REDUNDANT
| NIS | NON INTRINSICALLY SAFE | [5 empty] | NR: | NON-REDUNDANT
NOTE 1 : |  | GALVANIC ISOLATION BARRIER SHALL BE CONSIDERED FOR INTRINSICALLY SAFE (EEXia) LOOPS.
NOTE 2 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR ESD SYSTEM".
NOTE 3 : |  | DETAIL INFORMATION OF SYSTEM CABINETS AND MARSHALLING CABINETS INCLUDING: CABINET NAME, RACK AND SLOT NUMBERS, NUMBER OF CHANNELS, ADDRESS OF I/O SIGNALS, TERMINAL BLOCK STRIP NAMES, WHICH ARE SHOWN WITH “*” NOW, WILL BE COMPLETED IN CONTROL SYSTEM VENDORS DOCUMENTS.

## SUMMARY
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 5
9184 – 073 - 053 |  |  |  | BK |  | W007S | PEDCO | 110 | IN | LI | 0003 | D02
ESD I/O SUMMERY COUNT
| ITEM | I/O TYPE | IS/NIS |  | R/NR |  | DESCRIPTION | [5 empty] | QTY | REMARKS
| 1 | AI-IS-R | IS |  | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [5 empty] | 6 | NOTES 1,2
| 2 | AI-IS | IS |  | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [5 empty] | 0 | NOTES 1,2
| 3 | AO-IS-R | IS |  | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [5 empty] | 0 | NOTES 1,2
| 4 | AO-IS | IS |  | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [5 empty] | 0 | NOTES 1,2
| 5 | DI-NIS-R | NIS |  | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [5 empty] | 2 | NOTES 1,2
| 6 | DO-NIS-R | NIS |  | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE,REDUNDANT) | [5 empty] | 7 | NOTES 1,2
D02

## IO List for ESD System
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR ESD SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته |  |  | نوع مدرک |  |  | سریال |  |  | نسخه |  |  | شماره صفحه: 5 از 5
9184 – 073 - 053 |  |  | BK | W007S | PEDCO |  | 110 |  | IN |  |  | LI |  |  | 0003 |  |  | D02
I/O List For ESD System - Extension of Binak B/C Manifold
ITEM | TAG | DESCRIPTION | LOCATION | P&ID | SERVICE | I/O TYPE | SIGNAL TYPE | FROM | TO | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[10 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | LL | L | H | HH | IND/STA | COM.
1 | EZSO-1701A | Limit Switch Open | FROM W018S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701A | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
2 | EZSC-1701A | Limit Switch Close | FROM W018S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DI-NIS-R | 24VDC | EZSC-1701A | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
3 | PT-1701A | Pressure Transmitter | FROM W018S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | AI-IS-R | 4-20 mA | PT-1701A | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
4 | ESOV-1701A | Emergency Shutdown Solenoid Valve | FROM W018S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701A | * | * | * | * | * | * | * | * | [5 empty] | X
5 | EZSO-1701B | Limit Switch Open | FROM W046S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701B | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
6 | EZSC-1701B | Limit Switch Close | FROM W046S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DI-NIS-R | 24VDC | EZSC-1701B | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
7 | PT-1701B | Pressure Transmitter | FROM W046S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | AI-IS-R | 4-20 mA | PT-1701B | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
8 | ESOV-1701B | Emergency Shutdown Solenoid Valve | FROM W046S | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701B | * | * | * | * | * | * | * | * | [5 empty] | X
9 | EZSO-1701C | Limit Switch Open | FROM W008N | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701C | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
10 | EZSC-1701C | Limit Switch Close | FROM W008N | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DI-NIS-R | 24VDC | EZSC-1701C | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
11 | PT-1701C | Pressure Transmitter | FROM W008N | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | AI-IS-R | 4-20 mA | PT-1701C | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
12 | ESOV-1701C | Emergency Shutdown Solenoid Valve | FROM W008N | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701C | * | * | * | * | * | * | * | * | [5 empty] | X
13 | EZSO-1701D | Limit Switch Open | FROM W028 | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701D | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
14 | EZSC-1701D | Limit Switch Close | FROM W028 | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DI-NIS-R | 24VDC | EZSC-1701D | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
15 | PT-1701D | Pressure Transmitter | FROM W028 | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | AI-IS-R | 4-20 mA | PT-1701D | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
16 | ESOV-1701D | Emergency Shutdown Solenoid Valve | FROM W028 | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701D | * | * | * | * | * | * | * | * | [5 empty] | X
17 | EZSO-1701E | Limit Switch Open | FROM W035 | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701E | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
18 | EZIE-1701E | Limit Switch Close | FROM W035 | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DI-NIS-R | 24VDC | EZIE-1701E | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
19 | PT-1701E | Pressure Transmitter | FROM W035 | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | AI-IS-R | 4-20 mA | PT-1701E | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
20 | ESOV-1701E | Emergency Shutdown Solenoid Valve | FROM W035 | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701E | * | * | * | * | * | * | * | * | [5 empty] | X
21 | EZSO-1701F | Limit Switch Open | FROM W007S | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DI-NIS-R | 24VDC | EZSO-1701F | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
22 | EZSC-1701F | Limit Switch Close | FROM W007S | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DI-NIS-R | 24VDC | EZSC-1701F | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | DO2 DELETED
23 | PT-1701F | Pressure Transmitter | FROM W007S | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | AI-IS-R | 4-20 mA | PT-1701F | ESD | * | * | * | * | * | * | * | * | X |  |  | X | X
24 | ESOV-1701F | Emergency Shutdown Solenoid Valve | FROM W007S | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | ESOV-1701F | * | * | * | * | * | * | * | * | [5 empty] | X
25 | ESD-P-1701 | Emergency Shutdown Command | OIL SUMP | BK-W007S-PEDCO-110-PR-PI-0001 (6/6) | GAS | DO-NIS-R | 24VDC LOOP POWER | ESD | MCC(IRP) | * | * | * | * | * | * | * | * | [5 empty] | X
26 | ESDR -EXIST | Emergency Shutdown Command From Existing System | EXISTING SYSTEM | --- | --- | DI-NIS-R | 24VDC | Existing ESD | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
27 | ESDR 0-UPS | UPS FAILURE | UPS CHARGER | --- | --- | DI-NIS-R | 24VDC | UPS CHARGER | ESD | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 ADDED
D02
D02