## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0003_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0665 |  |  | Transmital Date: 2 Mar 2022
Document Title: I/O List For ESD Systems - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-IN-TR-0665 |  |  | Transmital Date: 2 Mar 2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-LI-0003_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | رديف شماره 4 اصلاح گردد. |  | BK-SUR-ENG-INS-00-03647 | 2022-03-16 | مدرک مطابق آخرین توافقات اصلاح شد.
2 | سيگنال هاي سريال در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03647 | 2022-03-16 | سیگنالهای سریالی درون سیستمی در io list دیده نمی شود.
3 | با توجه به اينكه مدارك پيش نياز اين مدرك مانند P&ID و Index نهايي نشده است. موارد در طول مهندسي تفصيلي نهايي خواهد شد. |  | BK-SUR-ENG-INS-00-03647 | 2022-03-16 | ملاحظه گردید. با توجه به اینکهNISOC خواستار AFC شدن این مدرک می باشد بنابراین این مدرک با اعمال اصلاحات AFC و ارسال گردید.
4 | ارتباطات بين سيستمي در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03647 | 2022-03-16 | مطابق آخرین توافقات اعمال شد.
5 | در صورتي كه در واحد موجود فرمان ESD صادر شود، در مورد sequence قطع اضطراري شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-INS-00-03647 | 2022-03-14 | یک سیگنال از سیستم ESD موجود به سیستم جدید ارسال شده که در ردیف 26 این مدرک آورده شده است و همچنین درمدرک ESD LEVEL HIERARCHY-EXTENSION OF BINAK B/C MANIFOLD تاثیر این سیگنال دیده شده است.
6
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 14 Mar 2022 |  |  |  |  | Date: