## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از6
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | ME | DT | 0002 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | AUG.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | JUN.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | APR.2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-707352
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 110 | ME | DT | 0002 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | [7 empty] | 67
4 | X | X | X |  | X |  |  |  | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X |  | X |  |  |  | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Note 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | SSGRL | PEDCO | 110 | ME | DT | 0002 | D03
General Notes
Rev
| 1. | The Asterisk * denotes information and/or confirmation required from VENDOR.
| 2. | The vendor shall be responsible for mechanical Strength of the equipment based on mentioned condition in data sheets.
| 3. | All nozzle locations and orientations to be confirmed by vendor.
| 4. | Instrumentation items are excluded from vendor's scope of supply.
| 5. | Any changes in material of construction, location & orientation of the nozzles shall be confirmed by client.
| 6. | All materials shall be new and unused.
| 7. | Prior to sealing the vessel for shipping and storage, the inside surface of the equipment shall be 100% visually inspected. Internal surfaces shall
be clean and thoroughly dried. The CLIENT or its nominated representative shall witness the cleanliness of internal suarfaces.
| 8. | Equipment packaging, preparation for shipment and delivery shal be in accordance with the project minimum requirements for"Packing,
Marking, Transportation Procedure (Doc. No. BK-GNRAL-PEDCO-000-QC-PR-0045)."
| 9. | Minimum spare part requirement for pre-commissioning, commissioning, start up and two years operation shall be in accordance with document
E&C-QC-SP-1.
| 10. | All nozzles must be vertical or horizontal and not perpendicular or parallel to vessel center line.
| 11. | All dimensions shown are in mm unless otherwise indicated. All nozzle sizes are in inch.
| 12. | The Tank shall be located under shelter.

## TANK
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: | [6 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 4 از 6
9184 – 073 - 053 | [6 empty] | BK | SSGRL | PEDCO | 110 |  | ME |  | DT | 0002 |  | D03
Mech. Data Sheet for Potable Water Tank of Well Pads (TK-1902)
Rev | DATA SHEET | [21 empty] | Rev
| 1 | Description | : |  | Potable Water Tank
| 2 | Tag No. | : |  | TK-1902, TK-2002, TK-2102, TK-2202, TK-1202, TK-1302 | [12 empty] | QTY |  | : | 6 | Set
| 3 | Type | : |  | Storage tank
| 4 | Process Design Data
| 5 | Contents |  |  |  | Water | [6 empty] | Corrosive / Erosive | [5 empty] | -
| 6 | Operating Temp. |  |  | (oC) | Amb. | [6 empty] | Nominal Tank Capacity |  |  | (m3) |  |  | 2.5
| 7 | Operating Press. |  | (barg) |  | ATM | [6 empty] | Liquid Sp. Gravity | [5 empty] | 1
| 8 | Mechanical Design Data
| 9 | Design Temp. | [7 empty] | (oC) |  |  | 55
| 10 | Design Press. | [7 empty] | (bar) |  |  | Full of water + Atm
| 11 | Vessel Orientation | [10 empty] | Vertical
| 12 | Working Liquid Capacity. | [8 empty] | (m3) |  | 2.1
| 13 | In. Dia. of Shell | [8 empty] | (mm) |  | By Vendor
| 14 | Tan/Tan Dim. | [7 empty] | (mm) |  |  | By Vendor
| 15 | Vessel Head Type | [10 empty] | By Vendor
| 16 | Vessel Construction | [7 empty] | (mm) |  |  | 5 Layers
| 17 | Ambient Temp. (Min. / Max) | [9 empty] | (oC) | -5 / 50
| 18 | Materials
| 19 | Shell | [10 empty] | HDPE
| 20 | Heads | [10 empty] | HDPE
| 21 | Nozzle Necks: | [10 empty] | HDPE
| 22 | Saddle | [10 empty] | HDPE
| 23 | Pipes | [10 empty] | HDPE
| 24 | Plates | [10 empty] | HDPE
| 25 | Flanges | [10 empty] | HDPE
| 26 | Fittings | [10 empty] | HDPE
| 27 | Lifting Lugs | [10 empty] | HDPE
| 28 | Name Plate Bracket | [10 empty] | HDPE
| 29 | Name Plate | [10 empty] | S.S. 316
| 30 | REFERENCE STANDARDS & DOCUMENTS
| 31 | Piping & Instrument Diagram (P&ID) for TK-1902 | [10 empty] | BK-BK05-PEDCO-110-PR-PI-0002
| 32 | Piping & Instrument Diagram (P&ID) for TK-2002 | [10 empty] | BK-BK12-PEDCO-110-PR-PI-0002
| 33 | Piping & Instrument Diagram (P&ID) for TK-2102 | [10 empty] | BK-BK14-PEDCO-110-PR-PI-0002
| 34 | Piping & Instrument Diagram (P&ID) for TK-2202 | [10 empty] | BK-BK15-PEDCO-110-PR-PI-0005
| 35 | Piping & Instrument Diagram (P&ID) for TK-1202 | [10 empty] | BK-W007S-PEDCO-110-PR-PI-0006
| 36 | Piping & Instrument Diagram (P&ID) for TK-1302 | [10 empty] | BK-W046S-PEDCO-110-PR-PI-0007
| 37 | Tank Color | [10 empty] | WHITE
| 38 | Fabrication and Inspection Requirements
| 39 | Tank shall be made in linear polyethwhich is a non e- toxic and food grad.
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
D03

## Sheet 1
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 | [6 empty] | BK |  | SSGRL | PEDCO | 110 |  | ME |  | DT | 0002 |  | D03
Data Sheets for Potable Water Tanks of Well Pads
Rev. | ACCESSORIES , NOZZLES LIST & LOADS @ BASE | [19 empty] | Rev.
| 1 | Accessories & Attachments
| 2 | Leg support | [8 empty] | Yes |  |  | Name Plate Bracket | [5 empty] | Yes
| 3 | Access Ladder & Platform | [8 empty] | Yes |  |  | Name Plate | [5 empty] | Yes
| 4 | Insulation Support | [8 empty] | No |  |  | Earthing Lug | [5 empty] | No
| 5 | Insulation | [8 empty] | No |  |  | Tailing Lug | [5 empty] | No
| 6 | Insulation Cover | [8 empty] | No |  |  | Cathodic Protection (Sacrificial Anodes) | [5 empty] | No
| 7 | Fireproofing Support | [8 empty] | No |  |  | Anchor Bolts . | [5 empty] | No
| 8 | Lifting Lugs | [8 empty] | Yes |  |  | Instrumentations | [5 empty] | No
| 9 | Internal/ External Clips | [8 empty] | No |  |  | Skid | [5 empty] | No
| 10 | Template | [8 empty] | No |  |  | Support Clips | [5 empty] | No
| 11 | Boot | [8 empty] | No |  |  | Vortex Breaker | [5 empty] | No
| 12 | Manvay Cover | [8 empty] | Yes |  |  | Rung & Grip | [5 empty] | No
| 13 | Internal Lining (By Painting) | [8 empty] | No |  |  | Heating Coil | [5 empty] | No
14
15
16
| 17 | Nozzles List * (Note 1)
| 18 | Mark |  | Qty. |  | Description |  |  |  | Pipe |  |  |  |  | Remark
| 19 | [8 empty] | Size |  | Proj.(mm)
| 20 |  | A | 1 |  | Inlet |  |  |  | 2" |  | By Vendor
| 21 |  | B 1 | 1 |  | Outlet |  |  |  | 2" |  | By Vendor
| 22 |  | B 2 | 1 |  | OVER FLOW |  |  |  | 2" |  | By Vendor
| 23 |  | V | 1 |  | Vent |  |  |  | 2" |  | By Vendor
| 24 |  | D | 1 |  | Drain |  |  |  | 2" |  | By Vendor
| 25 |  | L1,L2 | 2 |  | Level Gauge |  |  |  | 2" |  | By Vendor
| 26 |  | M | 1 |  | Manway |  |  |  | 18" |  | By Vendor
27
28
29
30
31
32
| 33 | WEIGHT CONTROL DATA SHEET SI UNIT * | [12 empty] | 1/1
34
35
36
37
| 38 | Service |  |  | : |  |  | Potable WATER tank | [6 empty] | Location |  | : | Bushehr (Binak Field)
| 39 | Type |  |  | : | [9 empty] | Quotation No. |  | :
| 40 | No. trains |  |  | : | [9 empty] | Serial No. |  | :
| 41 | No. stages |  |  | :
| 42 | Supplier |  |  | :
| 43 | Manufacturer |  |  | :
| 44 | Model |  |  | :
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61

## Sheet 2
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 | BK | SSGRL | PEDCO | 110 | ME | DT | 0002 | D03
Data Sheets for Potable Water Tanks of Well Pads
Sketch